–CHESS INTERLOCK CHECKOUT

Date: ____/___/____   Initials: ____/____

____ Retrieve interlock checkout keys (in 6 envelopes) and 3 lock blocks from Control Room

____ Ensure that interlock switch is on test (CESR control room)

____Ensure A-line PLC gets put in “test” mode (instructions on A-cave sheet, page 4)

____Conduct Complete CHESS INTERLOCK CHECKOUT

| CHESS West Area | CHESS East Area | CHESS G Area |
| --- | --- | --- |
| A Cave | D Line | G Line |
| A1 Station | D1 Station | G2 Cave |
| A2 Station | E Line | G1 Station |
| B Line | F Line | G2 Station |
| B1 Station | F1 Station | G3 Station |
| C Cave | F2 Station |  |
| C1 Station | F3 Station |  |

____ Secure CHESS West area for CESR interlock checkout

____ Leave Aux. Equipment jumpers in place for CESR interlock checkout. (Typically B-line, D-line and G-line but as many lines as possible)

____ Test all Dump buttons with interlocks on (see list on page 2). Verify that each dump panel (CHESS East, West, and G-line) will close area stops when dump panel for that area trips. NOTE: A1, D1, and F2 station panel dump buttons only close the station stops – not the area stops. A1, D1, and F2 station dump panels should be tested as part of the station interlock checkout. They have been removed from the list on page 2.

____ Return interlock checkout keys and lock blocks to Control Room after counting and inspecting.

DUMP BUTTONS

Verify that each dump panel (CHESS East, West, and G-line) will close area stops when dump panel for that area trips.

| WEST | EAST | G-Area |
| --- | --- | --- |
| ____A-Cave upstream ____A Cave downstream | ____D-Cave | ___G-Cave #1 |
|  |  | ___G-Cave #2 |
| ____A1 Station #1 | ____D1 North | ___G1 Panel |
| ____A1 Station #2 | ____D1 South | ___G1 #1 |
| ____A2 Panel | ____F-Cave upstream #1 | ___G1 #2 |
| ____A2 Station #1 | ____F-Cave downstream #2 | ___G1 #3 |
| ____A2 Station #2 | ____F-Cave downstream #3 | ___G1 #4 |
| ____A2 Station #3 | ____F1 Panel | ___G2 Panel |
| ____spare (jumpered) | ____F1 upstream | ___G2 #1 |
| ____ spare (jumpered) | ____F1 North | ___G2 #2 |
| ____B1 Panel | ____F1 downstream | ___G3 Panel |
| ____B1 upstream |  | ___G3 #1 |
| ____B1 middle | ____F2 upstream | ___G3 #2 |
| ____B1 downstream | ____F2 South | ___G3 #3 |
| ____spare (jumpered) | ____F2 downstream | ___G2-Cave Panel |
| ____C Cave #1 | ____F3 Panel |  |
| ____C Cave #2 | ____F3 upstream |  |
| ____C1 Panel |  |  |
| ____C1 Station #1 |  |  |
| ____C1 Station #2 |  |  |
| ____C1 Station #3 |  |  |

NOTES:

Jumpers

At the end of the CESR interlock checkout there is a test of the CHESS radiation chains

CHESS West and East:

- Remove area key from storage

- Open beamstops on at least one of the lines in the area

- Simulate a radiation monitor trip.

- CHESS beams stops and shutters should close, CESR beam killers close, and the linac is disabled.

- Open Beamstops on at least one of the lines in the area

- Create a loss of CHESS Area OK.

- CHESS beams stops and shutters should close, CESR beam killers close, and the linac is disabled.

G-Area

- Open beamstops on the G-line

- Simulate a radiation trip in the CESR control room

The results of these radiation chain checkouts is the disabling of the LINAC and closure of CESR beam-killers and closing of all CHESS beam stops and shutters.

Additional Interlock Checkouts to complete after an extended down period:

- F1 Liquid Nitrogen delivery system

- A1 Liquid Nitrogen delivery system

- A2 Liquid Nitrogen delivery system

- F2 cryo system

  - F-cave oxygen monitor

  - Dump buttons for cryo in: F cave, CHESS East roof, F2 cryo PLC

  - Thermostat in pan on CHESS East roof

- G3 Excimer Laser system

CHESS A-CAVE INTERLOCK CHECKOUT*
Date: ____/___/____  Initials: ____/____

| Procedure | Result |
| --- | --- |
| Put PLC at Ops in “test” mode. To get in test mode: Touch the “admin” tab at the top of the PLC. Enter password (found in general lock box). Touch the “test” tab. The buttons at the bottom of the “test” screen are toggle switches that allow the relay logic to be tested without software. When the “toggle switch” for shutter 1, shutter 2, and beamstop are green/on, the shutters and beamstop will open automatically when the line is secure. | ___Verify PLC is in “test” mode NOTE: Entire Checkout should be completed looking at the “test” screen ___Change shutters & beamstop toggles to green/on in the test screen |
| Remove CHESS area key from storage or have area in bypass (ie. the area is not secure) Open beamstop, line shutters, and station shutters Create loss of station OK for each station individually (i.e.. station door open and stops open ) | ___Line Shutters, Beamstop, Station Shutters close for A1 loss ___ Line Shutters, Beamstop, Station Shutters close for A2 loss |
| Open beamstop and line shutters Release US cave door micro switch 1 | ___Circuit 1 lost and Line Shutters and Beamstop close |
| Open beamstop and line shutters Release US cave door micro switch 2 | ___Circuit 2 lost and Line Shutters and Beamstop close |
| Open beamstop and line shutters Release DS cave door micro switch 1 | ___Circuit 1 lost and Line Shutters and Beamstop close |
| Open beamstop and line shutters Release DS cave door micro switch 2 | ___Circuit 2 lost and Line Shutters and Beamstop close |
| Open beamstop and line shutters Unlock US cave door | ___Circuit lost and Line Shutters and Beamstop close |
| Open beamstop and line shutters Unlock DS cave door | ___Circuit lost and Line Shutters and Beamstop close |
| CONTINUED ON NEXT PAGE | CONTINUED ON NEXT PAGE |
| NOTE: Labyrinth is located inside A1** Lock up cave Simulate cave labyrinth closed With beamstop and line shutters open, Release Labyrinth Door micro switch 1 | ___Circuit 1 lost and Line Shutters and Beamstop close |
| With beamstop open and line shutters open, Release Labyrinth Door micro switch 2 | ___Circuit 2 lost and Line Shutters and Beamstop close |
| Lock up labyrinth and cave doors Open beamstop and shutters and try to remove line key | ___No key solenoid enable |
| Close beamstop and line shutters Remove line key Attempt to open beamstop and shutters | ___Cannot open beamstop or line shutters |
| Take PLC at Ops out of “test” mode. Verify all buttons at the bottom of the “test” tab are red and “off.” Exit “test” mode by touching any display screen other than the “admin” tab or “test” tab | ___Verify PLC is out of “test” mode. |

NOTES
*Coordinate this with the first tests of A, A2
**This should be done in conjunction with the A1 check-out group since the labyrinth is located in A1.

Jumpers

CHESS A1 STATION INTERLOCK CHECKOUT*
Date: ____/___/____         Initials: ____/____

| Procedure | Result |
| --- | --- |
| Select the “control” tab on the A1 PLC screen | ___Verify PLC is displaying the “control” screen. |
| Simulate station doors closed Open station shutters Release US Door micro switch 1 | ___Circuit 1 lost and Shutters close** |
| Open station shutters Release US Door micro switch 2 | ___Circuit 2 lost and Shutters close** |
| Simulate station doors closed Open station shutters Release DS Door micro switch 1 | ___Circuit 1 lost and Shutters close** |
| Simulate station doors closed Open station shutters Release DS Door micro switch 2 | ___Circuit 2 lost and Shutters close** |
| Lock up station Open station shutters one at a time Try to remove station door key from panel | ___No key solenoid enable |
| Open station shutters one at a time Remove operator disable key on pane1 | ___Shutters close |
| w/ disable key out try to open shutters | ___No shutter enable |
| w/ station key out try to open shutters | ___No shutter enable |
| Lock up station Open station shutters one at a time Press Station Dump Button on station panel | ___Station dump circuits lost and shutters close |
| With Station Dump Button pressed in, try to open station shutters | ___No shutter enable, verify shutters won’t open |

NOTES
*This group should help with the A-cave group since the Cave labyrinth is located in A1.
**Lose station OK at station and line status panels. Line stops disabled

Jumpers

CHESS A2 STATION INTERLOCK CHECKOUT*
Date: ____/___/____   Initials: ____/____

| Procedure | Result |
| --- | --- |
| Simulate station doors closed Open station shutters Release Door micro switch 1 | ___Circuit 1 lost and shutters close* |
| Open station shutters Release Door micro switch 2 | ___Circuit 2 lost and shutters close* |
| Simulate labyrinth door 1 closed Open station shutters Release labyrinth door 1 micro switch 1 | ___Circuit 1 lost and shutters close* |
| Simulate labyrinth door 1 closed Open station shutters Release labyrinth door 1 micro switch 2 | ___Circuit 2 lost and shutters close* |
| Simulate labyrinth door 2 closed Open station shutters Release labyrinth door 2 micro switch 1 | ___Circuit 1 lost and shutters close* |
| Simulate labyrinth door 2 closed Open shutters Release labyrinth door 2 micro switch 2 | ___Circuit 2 lost and shutters close* |
| Lock up station Open station shutters one at a time Try to remove station door key from panel | ___No key solenoid enable |
| Open station shutters one at a time Remove operator disable key on pane1 | ___shutters close |
| w/ disable key out try to open shutters | ___No shutter enable |
| w/ station key out try to open shutters | ___No shutter enable |

NOTES
*Lose station OK at station and line status panels. Line stops disabled

Jumpers

CHESS B-LINE INTERLOCK CHECKOUT*
Date: ____/___/____  Initials: ____/____

| Procedure | Result |
| --- | --- |
| Open line stops Create loss of station OK i.e.. station door open and stops open (coordinate this with the tests of B1) | ___Line Stops close |
| Open line stops and remove line Op Dis. Key | ___Line Stops close |
| With Op Dis key removed attempt to open stops | ___Cannot open stops |

NOTES
*This should be done in conjunction with the B check-out.

Jumpers

CHESS B1 STATION INTERLOCK CHECKOUT
Date: ____/___/____  Initials: ____/____

| Procedure | Result |
| --- | --- |
| Simulate B1 upstream station door closed Open B1 station beam stops Release Door 1 micro switch 1 | ___Circuit 1 lost and beamstops close* |
| Simulate B1 upstream station door closed Open station beamstops Release Door 1 micro switch 2 | ___Circuit 2 lost and beamstops close* |
| Simulate B1 downstream station door closed Open B1 station beam stops Release Door 2 micro switch 1 | ___Circuit 1 lost and beamstops close* |
| Simulate B1 downstream station door closed Open station beamstops Release Door 2 micro switch 2 | ___Circuit 2 lost and beamstops close* |
| Simulate midstream labyrinth door 1 closed Open station shutters Release labyrinth door 1 micro switch 1 | ___Circuit 1 lost and shutters close* |
| Simulate midstream labyrinth door 1 closed Open station shutters Release labyrinth door 1 micro switch 2 | ___Circuit 2 lost and shutters close* |
| Simulate midstream labyrinth door 2 closed Open station shutters Release labyrinth door 2 micro switch 1 | ___Circuit 1 lost and shutters close* |
| Simulate midstream labyrinth door 2 closed Open station shutters Release labyrinth door 2 micro switch 2 | ___Circuit 2 lost and shutters close* |
| Simulate downstream labyrinth door 3 closed Open station shutters Release labyrinth door 3 micro switch 1 | ___Circuit 1 lost and shutters close* |
| Simulate downstream labyrinth door 3 closed Open shutters Release labyrinth door 3 micro switch 2 | ___Circuit 2 lost and shutters close* |
| Lock up station Open station beamstops one at a time Try to remove station door key from panel | ___No key solenoid enable |
| Open station beamstops one at a time Remove station disable key on pane1 | ___beamstops close |
| w/ disable key out try to open beamstops | ___No beamstop enable |
| w/ station key out try to open beamstops | ___No beamstop enable |

NOTES
*Lose station OK at station and line status panels. Line stops disabled

CHESS C-CAVE INTERLOCK CHECKOUT*
Date: ____/___/____  Initials: ____/____

| Procedure | Result |
| --- | --- |
| Open line stops Create loss of station OK i.e.. station door open and stops open (coordinate this with the first tests of C1) | ___Line Stops close* |
| Simulate cave door closed Open line stops Release door micro switch 1 | ___Circuit 1 lost and Shutters and stops close |
| Open line stops Release door micro switch 2 | ___Circuit 2 lost and Shutters and stops close |
| Open line stops Unlock door | ___Circuit lost and Shutters and stops close |
| With cave unlocked, try to open line stops and shutters | ___Cannot open stops or shutter |
| Lock up door Open line stops and shutter one at a time and try to remove line key | ___No key solenoid enable |
| Close line stops Remove line key Attempt to open stops and shutters | ___Cannot open stops or shutter |

NOTES
*This should be done in conjunction with the C1 check-out group.

Jumpers

CHESS C1 STATION INTERLOCK CHECKOUT
Date: ____/___/____  Initials: ____/____

NOTE: Need the white beam key from the safety lock box in order to open the station beamstops

| Procedure | Result |
| --- | --- |
| Simulate station doors closed Open station beamstops (white beam) Release Door micro switch 1 | ___Circuit 1 lost and beamstops close* |
| Simulate station door closed Open station beamstops (white beam) Release Door micro switch 2 | ___Circuit 2 lost and beamstops close* |
| Simulate station door closed Open station shutters (monochromatic beam) Release door micro switch 1 | ___Circuit 1 lost and shutters close* |
| Simulate station door closed Open station shutters (monochromatic beam) Release door micro switch 2 | ___Circuit 2 lost and shutters close* |
| Simulate labyrinth door closed Open station beamstops (white beam) Release labyrinth door micro switch 1 | ___Circuit 1 lost and beamstops close* |
| Simulate labyrinth door closed Open station beamstops (white beam) Release labyrinth door micro switch 2 | ___Circuit 2 lost and beamstops close* |
| Simulate labyrinth door closed Open station shutters (monochromatic beam) Release labyrinth door micro switch 1 | ___Circuit 1 lost and shutters close* |
| Simulate labyrinth door closed Open station shutters (monochromatic beam) Release labyrinth door micro switch 2 | ___Circuit 2 lost and shutters close* |
| Lock up station Open station beamstops & shutters one at a time Try to remove station door key from panel | ___No key solenoid enable |
| Open station beamstops and shutters Remove station disable key on pane1 | ___beamstops and shutters close |
| w/ disable key out try to open beamstops (white beam) | ___No beamstop enable |
| w/ disable key out try to open shutters (monochromatic) | ___No shutter enable |
| Open station beamstops (white beam) and remove white beam key | ___Beamstops close |
| W/ white beam key out try to open beamstops (white beam) | ___No beamstop enable |
| w/ station key out try to open beamstops (white beam) | ___No beamstop enable |
| w/ station key out try to open shutters(monochromatic) | ___No shutter enable |

NOTES
*Lose station OK at station and line status panels. Line stops

CHESS D-LINE INTERLOCK CHECKOUT*
Date: ____/___/____  Initials: ____/____

| Procedure | Result |
| --- | --- |
| Open line stops Create loss of station OK i.e.. station door open and stops open (coordinate this with the first tests of D1) | ___Line Stops close |
| Open line stops and remove line Op Dis. Key | ___Line Stops close |
| With Op Dis key removed attempt to open stops | ___Cannot open stops |

NOTES
*This should be done in conjunction with the D1 check-out group.

Jumpers

CHESS D1-STATION INTERLOCK CHECKOUT*
Date: ____/___/____  Initials: ____/____

| Procedure | Result |
| --- | --- |
| Select the “control” tab on the D1 PLC screen | ___Verify PLC is displaying the “control” screen |
| Simulate station door closed Open station Beamstops Release door micro switch 1 | ___Circuit 1 lost and Beamstops close** |
| Open station Beamstops Release door micro switch 2 | ___Circuit 2 lost and Beamstops close** |
| Close station door Simulate cave door closed Open station Beamstops Release cave door micro switch 1 | ___Circuit 1 lost and Beamstops close** |
| Simulate cave door closed Open station Beamstops Release cave door micro switch 2 | ___Circuit 2 lost and Beamstops close** |
| Simulate labyrinth door closed Open station Beamstops Release labyrinth micro switch 1 | ___Circuit 1 lost and Beamstops close** |
| Simulate labyrinth door closed Open station Beamstops Release labyrinth micro switch 2 | ___Circuit 2 lost and Beamstops close** |
| Lock up station Open station Beamstops one at a time Try to remove station door key from panel | ___No key solenoid enable |
| Open station Beamstops one at a time Remove station disable key on pane1 | ___Beamstops close |
| w/ disable key out try to open Beamstops | ___No beamstop enable |
| w/ station key out try to open Beamstops | ___No beamstop enable |
| Lock up station Open station Beamstops one at a time Press Station Dump Button on station panel | ___Station dump circuits lost and beamstops close |
| With Station Dump Button pressed in, try to open station beamstops | ___No beamstop enable, verify beamstops won’t open |

NOTES
*This group should help with the D-line group.
**Lose station OK at station and line status panels. Line stops disabled

CHESS E-LINE INTERLOCK CHECKOUT
Date: ____/___/____  Initials: ____/____

| Procedure | Result |
| --- | --- |
| Open line stops and remove line Op Dis. key | ___Line Stops close |
| With Op Dis key removed attempt to open stops | ___Cannot open stops |

NOTES

Jumpers

CHESS F-LINE INTERLOCK CHECKOUT*
Date: ____/___/____  Initials: ____/____

| Procedure | Result |
| --- | --- |
| Open line stops Create loss of station OK i.e.. station door open and stops open (coordinate this with the first tests of F1, F2 and F3) | ___Line Stops close* |
| Simulate cave doors closed Remember the search circuit on door lock Open line stops Release door micro switch 1 | ___Circuit 1 lost and Shutters and stops close |
| Open line stops Release door micro switch 2 | ___Circuit 2 lost and Shutters and stops close |
| Open line stops Unlock Door | ___Circuit lost and Shutters and stops close |
| Lock up doors Open line stops and shutter at panel with key switch repeat with additional panel and ensure that you can close stops from either location at all times | ___Function normally ___Function normally |
| Lock up doors Open line stops and shutter at panel without key switch repeat with additional panel and ensure that you can close stops from either location at all times | ___Close normally but only one beamstop will open ___Close normally but only one beamstop will open |
| Lock up doors Open line stops and shutter one at a time and try to remove line key (Test at both Ops and Remote Panel in East) | ___No key solenoid enable at remote panel ___No key solenoid enable at Ops panel |
| Close line stops Remove line key Attempt to open stops and shutters (test at both Ops and Remote Panel in East) | ___Cannot open stops or shutter from remote panel ___Cannot open stops or shutter from Ops panel |

NOTE: There is no reset button on the remote panel in CHESS East – need to reset from Ops when lose station OK 
*This should be done in conjunction with the F1, F2 and F3 check-out group.

CHESS F1 STATION INTERLOCK CHECKOUT*
Date: ____/___/____  Initials: ____/____

| Procedure | Result |
| --- | --- |
| Simulate station doors closed Open station shutters Release Door 1 micro switch 1 | ___Circuit 1 lost and Shutters close** |
| Open station shutters Release Door 1 micro switch 2 | ___Circuit 2 lost and Shutters close** |
| Lock up station Open station shutters one at a time Try to remove station door key from panel | ___No key solenoid enable |
| Open station shutters. Remove station disable key on pane1 | ___Shutters close |
| w/ disable key out try to open shutters | ___No shutter enable |

NOTES
*This group should help with the F-cave group.
**Lose station OK at station and line status panels. Line stops disabled

Jumpers

CHESS F2 STATION INTERLOCK CHECKOUT*
Date: ____/___/____  Initials: ____/____

| Procedure | Result |
| --- | --- |
| Select the “control” tab on the F2 PLC screen | ___Verify PLC is displaying the “control” screen. |
| Simulate station doors closed Open station shutters Release Door 1 micro switch 1 | ___Circuit 1 lost and Shutters close** |
| Open station shutters Release Door 1 micro switch 2 | ___Circuit 2 lost and Shutters close** |
| Lock up station Open station shutters one at a time Try to remove station door key from panel | ___No key solenoid enable |
| Open station shutters. Remove station disable key on pane1 | ___Shutters close |
| w/ disable key out try to open shutters | ___No shutter enable |
| Lock up station Open station shutters one at a time Press Station Dump Button on station panel | ___Station dump circuits lost and shutters close |
| With Station Dump Button pressed in, try to open station shutters | ___No shutter enable, verify shutters won’t open |

NOTES
* This group should help with the F-cave group.
**Lose station OK at station and line status panels. Line stops disabled

Jumpers

CHESS F3 STATION INTERLOCK CHECKOUT*
Date: ____/___/____  Initials: ____/____

| Procedure | Result |
| --- | --- |
| Simulate station doors closed Open station shutters Release Door 1 micro switch 1 | ___Circuit 1 lost and Shutters close** |
| Open station shutters Release Door 1 micro switch 2 | ___Circuit 2 lost and Shutters close** |
| Lock up station Open station shutters one at a time Try to remove station door key from panel | ___No key solenoid enable |
| Open station shutters. Remove station disable key on pane1 | ___Shutters close |
| w/ disable key out try to open shutters | ___No shutter enable |

NOTES
* This group should help with the F-cave group.
**Lose station OK at station and line status panels. Line stops disabled

Jumpers

CHESS G-LINE INTERLOCK CHECKOUT
Date: ____/___/____  Initials: ____/____

| Procedure | Result |
| --- | --- |
| Lock up G-cave Open line stops Create loss of station OK i.e.. station door open and stops open (coordinate this with the first tests of G1, G2, G2Cave and G3) | ___Line Stops close |
| Simulate cave door closed Open line stops Release door micro switch 1 | ___Circuit 1 lost and Shutters and stops close |
| Simulate cave door closed Open line stops Release door micro switch 2 | ___Circuit 2 lost and Shutters and stops close |
| Open line stops Unlock Door | ___Circuit lost and Shutters and stops close |
| Lock up doors Open line stops and shutter from G-ops Verify that you can close all stops from either G-ops or Ops panel at all times | ___Beamstops and shutter close from G-ops ___Beamstops and shutter close from Ops |
| Lock up doors Open line stops and shutter at panel without key switch | ___Beamstops and shutter will not open |
| Lock up doors Open line stops and shutter one at a time and try to remove line key | ___No key solenoid enable |
| Close line stops Remove line key Attempt to open stops and shutters | ___Cannot open stops or shutter |
| Reinsert line key and unlock cave | ___Cannot open stops or shutter |
| Open line stops Remove beam line operator disable key | ___beamstops close |
| w/ disable key out try to open beamstops | ___No beamstop enable |

NOTE: The remote panel at CHESS Ops does not work for opening stops, even when key switch is at Ops

CHESS G1 STATION INTERLOCK CHECKOUT
Date: ____/___/____  Initials: ____/____

| Procedure | Result |
| --- | --- |
| Simulate station doors closed Open station shutters Release Door 1 micro switch 1 | ___Circuit 1 lost and Shutters close** |
| Open station shutters Release Door 1 micro switch 2 | ___Circuit 2 lost and Shutters close** |
| Lock up station Open station shutters one at a time Try to remove station door key from panel | ___No key solenoid enable |
| Open station shutters. Remove station disable key on pane1 | ___Shutters close |
| w/ disable key out try to open shutters | ___No shutter enable |

NOTES
**Lose station OK at station and line status panels. Line stops disabled

Jumpers

CHESS G2 STATION INTERLOCK CHECKOUT*
Date: ____/___/____   Initials: ____/____

| Procedure | Result |
| --- | --- |
| Simulate station doors closed Open station shutters Release Door 1 micro switch 1 | ___Circuit 1 lost and Shutters close** |
| Open station shutters Release Door 1 micro switch 2 | ___Circuit 2 lost and Shutters close** |
| Lock up station Open station shutters one at a time Try to remove station door key from panel | ___No key solenoid enable |
| Open station shutters. Remove station disable key on pane1 | ___Shutters close |
| w/ disable key out try to open shutters | ___No shutter enable |

NOTES
**Lose station OK at station and line status panels. Line stops disabled

Jumpers

CHESS G2 CAVE INTERLOCK CHECKOUT*
Date: ____/___/____  Initials: ____/____

| Procedure | Result |
| --- | --- |
| Simulate station doors closed Open station shutters Release Door 1 micro switch 1 | ___Circuit 1 lost and Shutters close** |
| Open station shutters Release Door 1 micro switch 2 | ___Circuit 2 lost and Shutters close** |
| Lock up station Open station shutters one at a time Try to remove station door key from panel | ___No key solenoid enable |
| Open station shutters. Remove station disable key on pane1 | ___Shutters close |
| w/ disable key out try to open shutters | ___No shutter enable |

NOTES
**Lose station OK at station and line status panels. Line stops disabled

Jumpers

CHESS G3 STATION INTERLOCK CHECKOUT
Date: ____/___/____   Initials: ____/____

| Procedure | Result |
| --- | --- |
| Simulate station doors closed Open station shutters Release Door 1 micro switch 1 | ___Circuit 1 lost and Shutters close** |
| Open station shutters Release Door 1 micro switch 2 | ___Circuit 2 lost and Shutters close** |
| Lock up station Open station shutters one at a time Try to remove station door key from panel | ___No key solenoid enable |
| Open station shutters. Remove station disable key on pane1 | ___Shutters close |
| w/ disable key out try to open shutters | ___No shutter enable |

NOTES
**Lose station OK at station and line status panels. Line stops disabled

Jumpers

Revisions:

Rev. 1 – Initial Document transferred from old CHESS training site

Rev. 2 – Clarified instructions based on feedback from users of this document (1/18/13 ZB)

Rev. 3 – Changed A-line checklist to reflect new changes from A-line upgrade and PLC control of beamstops and shutters. Updated dump button checklist to reflect changes from A-line upgrade (9/5/14 KM)

Rev. 4 – Reorganized A-cave checklist to include steps about putting PLC in test mode. Clarified steps on A-cave and C-line lists based on feedback from users of this document. Removed steps about red tag on LINAC from first page (not a CHESS responsibility). (1/8/15 KM)

Rev. 5 – Clarified instructions for A-line based on feedback from users of this document. Added to F-cave checklist: checking both the remote panel and the panel at Ops for the last 2 steps (5/11/15 KM)

Rev. 6 – Clarified instructions for C-line (white beam beamstops and monochromatic beam shutters) based on feedback. Re-worded one step for A-line for clarity. Added note on dump button page to verify each dump panel will close area beamstops when it trips. (09/08/15 KM)

Rev. 7 – Removed A1 panel, D1 panel, and F2 panel from dump button checklist. Added new steps to A1, D1, F2 station checklists for verifying station panel dump buttons close the station stops. (10/3/16 KMM)

Rev. 8 – Edited G-line checklist – removed step for trying to open beamstops remotely from CHESS Ops panel, as that panel does not work. (10/6/16 KMM)

Rev. 9 – Edited A1, D1, and F2 checklists – added a verification step for selecting the “control” tab on each respective PLC screen (1/24/17 AK)