ILC Damping Rings Component/Subsystem Specification

Part I – Classification Information

| Component Description: | Power Supply for 6 m Dipoles |  |  |  |
| --- | --- | --- | --- | --- |
| Component Location (beamline): | EDR/PDR I/PDR II | Lattice Version: |  | OCS6, 2006-06-20 |
| Document Number: | EDR-MAG-mspy-001 |  | Date: | 2006-08-03 |
| Prepared by: | Andy Wolski |  | email: | a.wolski@dl.ac.uk |
| Technical/Global System: | Magnets |  |  |  |
| Technical/Global System Contact: | John Tompkins |  | email: | jct@fnal.gov |
| DR Area System Contact: | Jie Gao Mike Zisman |  | email: | gaoj@ihep.ac.cn mszisman@lbl.gov |

Part II – Main Parameters

| Parameter | Value | # Reference |
| --- | --- | --- |
| Quantity per beamline | 6 | [1] |
| Number of dipoles supplied per power supply | 19 | [1] |
| Maximum current | 520 A | [2] |
| Voltage drop per dipole at maximum current | 15 V | [2] |
| Cable length (maximum) | 2134 m | [1] |
| Voltage drop per unit cable length | 22.5 V/km | [1] |
| Total voltage | 333 V | [1] |
| Total power output | 174 kW |  |
| Unipolar/bipolar | Unipolar | [3] |
| Unit Cost | Public version: no costs shown | [3] |

Part III – Other Parameters, Information, and Drawings

ILC Damping Rings Component Specification

| Document Number: | EDR-MAG-mspy-001 | Date: | 2006-08-03 |
| --- | --- | --- | --- |

Part IV – References

[1]	EDR-MAG-cbl-001

[2]	EDR-MAG-dip-001

[3]	J. Chen and J. Gao, “Magnet Power System Data for Damping Rings”, 4 July 2006.