ILC Damping Rings Component/Subsystem Specification

Part I – Classification Information

| Component Description: | Electron damping ring klystron HV power supply (modulator) |  |  |  |
| --- | --- | --- | --- | --- |
| Component Location (beamline): | EDR | Lattice Version: |  | OCS2, March 2006 |
| Document Number: | EDR-RF-hvps-001 |  | Date: | 2006-06-12 |
| Prepared by: | Roberto Boni |  | email: | roberto.boni@lnf.infn.it |
| Technical/Global System: | RF Systems |  |  |  |
| Technical/Global System Contact: |  |  | email: |  |
| DR Area System Contact: | Susanna Guiducci |  | email: | susanna.guiducci@lnf.infn.it |

Part II – Main Parameters

| Parameter | # Value |  | # Reference |
| --- | --- | --- | --- |
| Quantity per beamline | 8 | (7) | [1] |
| Max output DC power | 1300 kW |  |  |
| Efficiency | 90 % |  |  |
| Max output voltage | 75 kV |  |  |
| Max output current | 17 A |  |  |
| Wall plug voltage | 380V- 3 phases (50 – 60 Hz) |  |  |
| Wall plug power | 1500 kVA |  |  |
| Unit Cost per modulator | Public version: no cost shown |  |  |

Part III – Other Parameters, Information, and Drawings

ILC Damping Rings Component Specification

| Document Number: | EDR-RF-hvps-001 | Date: | 2006-06-12 |
| --- | --- | --- | --- |

Part IV – References

[1]	Total cost should be based on 8 P.S. (modulators) in EDR.  Performance specification based on being able to operate with 7 RF stations running.

[2]	R. Boni, G. Cavallari, RF System for the ILC Damping Rings, ILC-LNF-001, Tech. Note, June 2006.