## Power Calculations
|  |  | Power Input [kW] | Power Output Distribution [kW] |  |  |  | Power Output [kW]
|  |  |  | Magnets |  | Cables | Power Supply Losses
|  |  |  | Water | Air
Alcove Locations
Alcove 1 | 1018 | meters
Alcove 2 | 2334 | meters
Alcove 3 | 4370 | meters
Alcove 4 | 5686 | meters
Total Dipole Power |  |  | 1581.3195 | 1332.6 | 0 | 42.4604 | 206.2591 | 1581.3195
6 m Dipoles (N. Morozov v2 C-style)
Current | 320 | amperes
Power per dipole | 11.1 | kW
Number of dipoles | 114
Total 6 m Dipole Power | 1265.4 | kW |  | 1265.4
3 m Dipoles (N. Morozov v2 C-style)
Current | 320 | amperes
Power per dipole | 5.6 | kW
Number of dipoles | 12
Total 3 m Dipole Power | 67.2 | kW |  | 67.2
Dipole Cables
Total length | 10000 | meters
Cable gauge | -9 | AWG
Cable resistance | 0.041465 | ohm/km
Current | 320 | amperes
Total Dipole Cable Power | 42.4604 | kW |  |  |  | 42.4604
Dipole Power Supplies
Magnet + cable power | 1375.0604 | kW
Power supply efficiency | 85 | %
Total Dipole Power Supply Power | 206.2591 | kW |  |  |  |  | 206.2591
Total Wiggler Power |  |  | 257.1709 | 257.1709 |  | 105.366 | 15.8049 | 378.3418
Wiggler Power
Current | 118 | amperes
Number of Wigglers | 80
Cryogenic Wall Power per meter | 0.68 | kW
Total wiggler length | 200 | meters
Wiggler Cables
Total length | 36000 | meters
Cable gauge | -2 | AWG
Cable resistance | 0.2102 | ohm/km
Current | 118 | amperes
Total Wiggler Cable Power | 105.366 | kW |  |  |  | 105.366
Wiggler Power Supplies
Magnet + cable power | 105.366 | kW
Power supply efficiency | 85 | %
Total Wiggler Power Supply Power | 15.8049 | kW |  |  |  |  | 15.8049
Total Quadrupole Power |  |  | 403.2684 | 144.5687 | 45.922 | 160.1775 | 52.6002 | 403.2684
High Field Quadrupole Power
Pole-tip radius | 0.03 | meters
Pole-tip field at maximum design current | 0.517 | tesla
Length | 0.3 | meters
Beam energy | 5 | GeV
Beam rigidity | 16.6782 | tesla-meters
k1L at maximum design current | 0.30998 | /meters^2
Maximum design current | 146 | amperes
Voltage at maximum design current | 15.6 | volts
Cable gauge | -2 | AWG
Cable resistance | 0.2102 | ohm/km
Power supply efficiency | 85 | %
Low Field Quadrupole Power
Pole-tip radius | 0.03 | meters
Pole-tip field at maximum design current | 0.198 | tesla
Length | 0.3 | meters
Beam energy | 5 | GeV
Beam rigidity | 16.6782 | tesla-meters
k1L at maximum design current | 0.11872 | /meters^2
Maximum design current | 8.1 | amperes
Voltage at maximum design current | 20 | volts
Cable gauge | -2 | AWG
Cable resistance | 0.2102 | ohm/km
Power supply efficiency | 85 | %
Total Sextupole Power |  |  | 8.289 |  | 0.82018 | 6.3505 | 1.0756 | 8.2463
Pole-tip radius | 0.03 | meters
Pole-tip field at maximum design current | 0.00756 | tesla
Length | 0.3 | meters
Beam energy | 5 | GeV
Beam rigidity | 16.6782 | tesla-meters
k2L at maximum design current | 0.30219 | /meters^2
Maximum design current | 7.2 | amperes
Voltage at maximum design current | 0.53 | volts
Cable gauge | 3 | AWG
Cable resistance | 0.67015 | ohm/km
Power supply efficiency | 85 | %
Total Corrector Magnets Power |  |  | 70.4416 |  | 43.2 | 16.6754 | 10.5662 | 70.4416
Maximum current | 9.6 | amperes
Voltage at maximum current | 15 | volts
Power per corrector at maximum current | 0.144 | kW
Cable gauge | 3 | AWG
Cable resistance | 0.67015 | ohm/km
Average cable length | 450 | meters
Average power per corrector cable at maximum current | 0.055585 | kW
Power per corrector plus cable at maximum current | 0.19958 | kW
Power supply efficiency | 85 | %
Number of correctors (horizontal and vertical) | 300
Total Skew Quadrupole Power |  |  | 29.041 |  | 12.96 | 11.7249 | 4.3562 | 29.041
Maximum current | 9 | amperes
Voltage at maximum current | 6 | volts
Power per corrector at maximum current | 0.054 | kW
Cable gauge | 3 | AWG
Cable resistance | 0.67015 | ohm/km
Average cable length | 450 | meters
Average power per corrector cable at maximum current | 0.048854 | kW
Power per corrector plus cable at maximum current | 0.10285 | kW
Power supply efficiency | 85 | %
Number of correctors (horizontal and vertical) | 240
Total Average Fast Kicker Power |  |  | 442.7294 | 442.7294 | 0 |  |  | 442.7294
Pulse amplitude | 280 | kV
Pulse length | 4 | ns
Pulses per second | 30000
Duty factor | 0.00012
Impedance | 50 | ohms
Average power | 188.16 | kW
Pulser efficiency | 85 | %
Total Septa Power |  |  | 46 | 46 | 0 |  |  | 46
Total Magnets Power |  |  | 2434.9915 | 2223.069 | 102.9022 | 342.7547 | 290.6622 | 2959.388

## Cable Gauge Tables
Electrical Conductivity | 55950000 | /Ohm-m
Density | 8920 | kg/m3
Cost | 0 | $/tonne
Gauge (AWG) | Cable Diameter [mm] | Cable Resistance [Ohm/km] | Cable Mass [kg/m] | Conductor Cost [$/m]
-15 | 46.9714 | 0.010314 | 15.4569 | 0
-14 | 41.8293 | 0.013006 | 12.2579 | 0
-13 | 37.2501 | 0.0164 | 9.7209 | 0
-12 | 33.1721 | 0.020681 | 7.7091 | 0
-11 | 29.5406 | 0.026078 | 6.1136 | 0
-10 | 26.3067 | 0.032883 | 4.8483 | 0
-9 | 23.4268 | 0.041465 | 3.8449 | 0 | Dipole cables
-8 | 20.8622 | 0.052287 | 3.0491 | 0
-7 | 18.5783 | 0.065932 | 2.4181 | 0
-6 | 16.5444 | 0.083139 | 1.9176 | 0
-5 | 14.7333 | 0.10484 | 1.5207 | 0
-4 | 13.1203 | 0.1322 | 1.206 | 0
-3 | 11.684 | 0.1667 | 0.9564 | 0
-2 | 10.4049 | 0.2102 | 0.75846 | 0
-1 | 9.2658 | 0.26506 | 0.60148 | 0
0 | 8.2515 | 0.33423 | 0.477 | 0 | Quadrupole, corrector and skew quad cables
1 | 7.3481 | 0.42146 | 0.37828 | 0
2 | 6.5437 | 0.53145 | 0.29999 | 0
3 | 5.8273 | 0.67015 | 0.2379 | 0 | Sextupole cables

## Quadrupoles
Name | Quad Type (LO or HI Field) | s [m] | Length [m] | k1L [m^-2] | Current [A] | Voltage [V] | Magnet Power [kW] | Nearest Alcove [m] | Total Cable Voltage [V] | Total Cable Power [kW] | Power Supply Loss [kW] | Total Power [kW] | Power Supply 0-1 kW | Power Supply 1-5 kW | Power Supply 5-20 kW |  | QFI | QDI | QDMS2 | QFMS2 | QDMS1 | QFMS1 | QFMA1 | QDMA1 | QDA | QFA | QFMT1 | QDMT1 | QFMA2 | QDMA2 | QFMA3 | QDMA3 | QFMT2 | QDMT2 | QFWH | QDRF | QFRF | QDWH | QFMINJ1 | QDMINJ1 | QFMINJ2 | QDMINJ2 | QFMINJ3 | QDMINJ3 | QFINJ4H | QDINJ2 | QFINJ3 | QFINJ1 | QDINJ1 | QFINJ2H
QFI | LO | 0.15 | 0.15 | 0.038374 | 2.6183 | 6.4648 | 0.016927 | 1017.85 | 1.1204 | 0.0029334 | 0.002979 | 0.022839 | 1 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDI | LO | 13.71 | 0.3 | -0.070481 | 4.8089 | 11.8738 | 0.0571 | 1004.29 | 2.0303 | 0.0097636 | 0.010029 | 0.076893 | 1 | 0 | 0 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFI | LO | 27.27 | 0.3 | 0.076749 | 5.2365 | 12.9296 | 0.067706 | 990.73 | 2.181 | 0.011421 | 0.011869 | 0.090996 | 1 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDI | LO | 40.83 | 0.3 | -0.070481 | 4.8089 | 11.8738 | 0.0571 | 977.17 | 1.9755 | 0.0095 | 0.0099899 | 0.076589 | 1 | 0 | 0 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFI | LO | 54.39 | 0.3 | 0.076749 | 5.2365 | 12.9296 | 0.067706 | 963.61 | 2.1213 | 0.011108 | 0.011822 | 0.090637 | 1 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDI | LO | 67.95 | 0.3 | -0.070481 | 4.8089 | 11.8738 | 0.0571 | 950.05 | 1.9207 | 0.0092363 | 0.0099504 | 0.076286 | 1 | 0 | 0 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFI | LO | 81.51 | 0.3 | 0.076749 | 5.2365 | 12.9296 | 0.067706 | 936.49 | 2.0616 | 0.010796 | 0.011775 | 0.090277 | 1 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDI | LO | 95.07 | 0.3 | -0.070481 | 4.8089 | 11.8738 | 0.0571 | 922.93 | 1.8658 | 0.0089726 | 0.0099108 | 0.075983 | 1 | 0 | 0 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFI | LO | 108.63 | 0.3 | 0.076749 | 5.2365 | 12.9296 | 0.067706 | 909.37 | 2.0019 | 0.010483 | 0.011728 | 0.089918 | 1 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDI | LO | 122.19 | 0.3 | -0.070481 | 4.8089 | 11.8738 | 0.0571 | 895.81 | 1.811 | 0.008709 | 0.0098713 | 0.07568 | 1 | 0 | 0 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFI | LO | 135.75 | 0.3 | 0.076749 | 5.2365 | 12.9296 | 0.067706 | 882.25 | 1.9422 | 0.01017 | 0.011681 | 0.089558 | 1 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDI | LO | 149.31 | 0.3 | -0.070481 | 4.8089 | 11.8738 | 0.0571 | 868.69 | 1.7562 | 0.0084453 | 0.0098317 | 0.075377 | 1 | 0 | 0 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFI | LO | 162.87 | 0.3 | 0.076749 | 5.2365 | 12.9296 | 0.067706 | 855.13 | 1.8825 | 0.0098578 | 0.011635 | 0.089199 | 1 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMS2 | LO | 174.2423 | 0.3 | -0.087962 | 6.0016 | 14.8187 | 0.088936 | 843.7577 | 2.1289 | 0.012777 | 0.015257 | 0.11697 | 1 | 0 | 0 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMS2 | LO | 180.4473 | 0.3 | 0.070722 | 4.8253 | 11.9143 | 0.05749 | 837.5527 | 1.699 | 0.0081984 | 0.0098533 | 0.075542 | 1 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMS1 | HI | 196.4803 | 0.3 | -0.13416 | 63.1859 | 6.7514 | 0.42659 | 821.5197 | 21.8224 | 1.3789 | 0.27082 | 2.0763 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMS1 | HI | 197.7803 | 0.3 | 0.10471 | 49.3192 | 5.2697 | 0.2599 | 820.2197 | 17.0063 | 0.83874 | 0.1648 | 1.2634 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA1 | LO | 208.5903 | 0.3 | 0.099551 | 6.7923 | 16.7711 | 0.11391 | 809.4097 | 2.3113 | 0.015699 | 0.019442 | 0.14905 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA1 | LO | 212.4903 | 0.3 | -0.079158 | 5.4009 | 13.3356 | 0.072024 | 805.5097 | 1.8289 | 0.009878 | 0.012285 | 0.094188 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 229.0903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 788.9097 | 1.9481 | 0.011443 | 0.014495 | 0.11113 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 232.9903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 785.0097 | 1.9272 | 0.011254 | 0.014318 | 0.10977 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 247.4903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 770.5097 | 1.8916 | 0.011046 | 0.014287 | 0.10953 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 251.3903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 766.6097 | 1.893 | 0.011119 | 0.014446 | 0.11075 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 267.9903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 750.0097 | 1.852 | 0.010878 | 0.01441 | 0.11048 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 271.8903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 746.1097 | 1.8317 | 0.010696 | 0.014234 | 0.10913 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 286.3903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 731.6097 | 1.7961 | 0.010488 | 0.014203 | 0.10889 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 290.2903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 727.7097 | 1.797 | 0.010555 | 0.014361 | 0.1101 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 306.8903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 711.1097 | 1.756 | 0.010314 | 0.014325 | 0.10983 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 310.7903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 707.2097 | 1.7362 | 0.010139 | 0.014151 | 0.10849 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 325.2903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 692.7097 | 1.7006 | 0.0099308 | 0.01412 | 0.10825 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 329.1903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 688.8097 | 1.7009 | 0.0099907 | 0.014277 | 0.10946 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 345.7903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 672.2097 | 1.6599 | 0.0097499 | 0.014241 | 0.10918 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 349.6903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 668.3097 | 1.6407 | 0.009581 | 0.014067 | 0.10785 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 364.1903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 653.8097 | 1.6051 | 0.0093731 | 0.014036 | 0.10761 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 368.0903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 649.9097 | 1.6048 | 0.0094265 | 0.014192 | 0.10881 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 384.6903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 633.3097 | 1.5639 | 0.0091857 | 0.014156 | 0.10853 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 388.5903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 629.4097 | 1.5452 | 0.0090233 | 0.013983 | 0.10721 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 403.0903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 614.9097 | 1.5096 | 0.0088154 | 0.013952 | 0.10697 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 406.9903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 611.0097 | 1.5088 | 0.0088623 | 0.014108 | 0.10816 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 423.5903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 594.4097 | 1.4678 | 0.0086215 | 0.014071 | 0.10788 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 427.4903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 590.5097 | 1.4497 | 0.0084656 | 0.0139 | 0.10657 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 441.9903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 576.0097 | 1.4141 | 0.0082577 | 0.013869 | 0.10633 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 445.8903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 572.1097 | 1.4127 | 0.0082981 | 0.014023 | 0.10751 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 462.4903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 555.5097 | 1.3717 | 0.0080573 | 0.013987 | 0.10723 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 466.3903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 551.6097 | 1.3542 | 0.0079079 | 0.013816 | 0.10592 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 480.8903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 537.1097 | 1.3186 | 0.0077001 | 0.013785 | 0.10569 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 484.7903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 533.2097 | 1.3167 | 0.0077338 | 0.013938 | 0.10686 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 501.3903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 516.6097 | 1.2757 | 0.0074931 | 0.013902 | 0.10658 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 505.2903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 512.7097 | 1.2587 | 0.0073503 | 0.013733 | 0.10528 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 519.7903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 498.2097 | 1.2231 | 0.0071424 | 0.013701 | 0.10504 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 523.6903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 494.3097 | 1.2206 | 0.0071696 | 0.013854 | 0.10621 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 540.2903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 477.7097 | 1.1796 | 0.0069288 | 0.013818 | 0.10593 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 544.1903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 473.8097 | 1.1632 | 0.0067926 | 0.013649 | 0.10464 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 558.6903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 459.3097 | 1.1276 | 0.0065847 | 0.013618 | 0.1044 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 562.5903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 455.4097 | 1.1246 | 0.0066054 | 0.013769 | 0.10556 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 579.1903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 438.8097 | 1.0836 | 0.0063646 | 0.013733 | 0.10529 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 583.0903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 434.9097 | 1.0677 | 0.0062349 | 0.013565 | 0.104 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 597.5903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 420.4097 | 1.0321 | 0.006027 | 0.013534 | 0.10376 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 601.4903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 416.5097 | 1.0285 | 0.0060412 | 0.013684 | 0.10491 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 618.0903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 399.9097 | 0.98751 | 0.0058004 | 0.013648 | 0.10464 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 621.9903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 396.0097 | 0.97219 | 0.0056772 | 0.013482 | 0.10336 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 636.4903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 381.5097 | 0.9366 | 0.0054694 | 0.01345 | 0.10312 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 640.3903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 377.6097 | 0.93245 | 0.005477 | 0.0136 | 0.10426 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 656.9903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 361.0097 | 0.89145 | 0.0052362 | 0.013564 | 0.10399 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 660.8903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 357.1097 | 0.8767 | 0.0051196 | 0.013398 | 0.10272 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 675.3903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 342.6097 | 0.8411 | 0.0049117 | 0.013367 | 0.10248 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 679.2903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 338.7097 | 0.83639 | 0.0049127 | 0.013515 | 0.10362 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 695.8903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 322.1097 | 0.7954 | 0.004672 | 0.013479 | 0.10334 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 699.7903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 318.2097 | 0.7812 | 0.0045619 | 0.013314 | 0.10208 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 714.2903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 303.7097 | 0.7456 | 0.004354 | 0.013283 | 0.10184 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 718.1903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 299.8097 | 0.74033 | 0.0043485 | 0.01343 | 0.10297 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 734.7903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 283.2097 | 0.69934 | 0.0041078 | 0.013394 | 0.10269 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 738.6903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 279.3097 | 0.6857 | 0.0040042 | 0.013231 | 0.10143 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 753.1903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 264.8097 | 0.6501 | 0.0037963 | 0.013199 | 0.1012 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 757.0903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 260.9097 | 0.64427 | 0.0037843 | 0.013346 | 0.10232 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 773.6903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 244.3097 | 0.60328 | 0.0035435 | 0.01331 | 0.10204 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 777.5903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 240.4097 | 0.5902 | 0.0034465 | 0.013147 | 0.10079 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 792.0903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 225.9097 | 0.5546 | 0.0032387 | 0.013116 | 0.10055 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 795.9903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 222.0097 | 0.54822 | 0.0032201 | 0.013261 | 0.10167 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 812.5903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 205.4097 | 0.50723 | 0.0029793 | 0.013225 | 0.10139 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 816.4903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 201.5097 | 0.4947 | 0.0028889 | 0.013063 | 0.10015 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 830.9903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 187.0097 | 0.4591 | 0.002681 | 0.013032 | 0.099913 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 834.8903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 183.1097 | 0.45216 | 0.0026559 | 0.013177 | 0.10102 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 851.4903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 166.5097 | 0.41117 | 0.0024151 | 0.01314 | 0.10074 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 855.3903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 162.6097 | 0.3992 | 0.0023312 | 0.01298 | 0.099511 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 869.8903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 148.1097 | 0.36361 | 0.0021233 | 0.012948 | 0.099272 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 873.7903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 144.2097 | 0.3561 | 0.0020917 | 0.013092 | 0.10037 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 890.3903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 127.6097 | 0.31511 | 0.0018509 | 0.013056 | 0.10009 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 894.2903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 123.7097 | 0.3037 | 0.0017735 | 0.012896 | 0.09887 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 908.7903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 109.2097 | 0.26811 | 0.0015656 | 0.012865 | 0.09863 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 912.6903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 105.3097 | 0.26005 | 0.0015274 | 0.013007 | 0.099723 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 929.2903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 88.7097 | 0.21905 | 0.0012867 | 0.012971 | 0.099446 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 933.1903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 84.8097 | 0.20821 | 0.0012158 | 0.012812 | 0.098228 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 947.6903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 70.3097 | 0.17261 | 0.001008 | 0.012781 | 0.097989 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 951.5903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 66.4097 | 0.16399 | 0.00096323 | 0.012923 | 0.099074 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 968.1903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 49.8097 | 0.123 | 0.00072245 | 0.012887 | 0.098797 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 972.0903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 45.9097 | 0.11271 | 0.00065817 | 0.012729 | 0.097587 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 986.5903 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 31.4097 | 0.07711 | 0.00045029 | 0.012698 | 0.097348 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 990.4903 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 27.5097 | 0.067931 | 0.00039901 | 0.012838 | 0.098425 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA1 | LO | 1007.0903 | 0.3 | -0.079158 | 5.4009 | 13.3356 | 0.072024 | 10.9097 | 0.024771 | 0.00013379 | 0.010824 | 0.082982 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA1 | LO | 1010.9903 | 0.3 | 0.099551 | 6.7923 | 16.7711 | 0.11391 | 7.0097 | 0.020016 | 0.00013595 | 0.017108 | 0.13116 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMT1 | HI | 1022.3003 | 0.3 | 0.16088 | 75.773 | 8.0963 | 0.61348 | 4.3003 | 0.13699 | 0.01038 | 0.093579 | 0.71744 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMT1 | HI | 1025.2503 | 0.3 | -0.18947 | 89.2401 | 9.5352 | 0.85093 | 7.2503 | 0.27201 | 0.024274 | 0.13128 | 1.0065 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA2 | HI | 1038.7503 | 0.3 | 0.16713 | 78.7149 | 8.4106 | 0.66204 | 20.7503 | 0.68667 | 0.054051 | 0.10741 | 0.82351 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA2 | HI | 1049.2803 | 0.3 | -0.1468 | 69.1418 | 7.3878 | 0.5108 | 31.2803 | 0.90923 | 0.062866 | 0.08605 | 0.65972 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA3 | HI | 1060.8323 | 0.3 | 0.10723 | 50.5027 | 5.3962 | 0.27252 | 42.8323 | 0.90939 | 0.045927 | 0.047767 | 0.36622 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA3 | HI | 1071.9323 | 0.3 | -0.12488 | 58.8168 | 6.2845 | 0.36964 | 53.9323 | 1.3336 | 0.078436 | 0.067211 | 0.51528 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMT2 | HI | 1079.3323 | 0.3 | 0.13944 | 65.6748 | 7.0173 | 0.46086 | 61.3323 | 1.6934 | 0.11121 | 0.085811 | 0.65788 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMT2 | HI | 1087.6323 | 0.3 | -0.13006 | 61.2584 | 6.5454 | 0.40096 | 69.6323 | 1.7932 | 0.10985 | 0.076622 | 0.58744 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 1096.8323 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 78.8323 | 3.0744 | 0.2852 | 0.18071 | 1.3854 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDRF | HI | 1100.5923 | 0.3 | -0.19873 | 93.5985 | 10.0009 | 0.93607 | 82.5923 | 3.2499 | 0.30419 | 0.18604 | 1.4263 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFRF | HI | 1104.3523 | 0.3 | 0.21047 | 99.1305 | 10.592 | 1.05 | 86.3523 | 3.5987 | 0.35674 | 0.21101 | 1.6177 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDRF | HI | 1108.1123 | 0.3 | -0.19873 | 93.5985 | 10.0009 | 0.93607 | 90.1123 | 3.5458 | 0.33188 | 0.19019 | 1.4581 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 1111.8723 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 93.8723 | 3.661 | 0.33962 | 0.18887 | 1.448 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 1115.6223 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 97.6223 | 3.4544 | 0.29076 | 0.15716 | 1.2049 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 1119.3723 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 101.3723 | 3.9535 | 0.36675 | 0.19294 | 1.4792 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 1123.1223 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 105.1223 | 3.7198 | 0.31309 | 0.16051 | 1.2306 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 1126.8723 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 108.8723 | 4.2459 | 0.39388 | 0.19701 | 1.5104 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 1130.6223 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 112.6223 | 3.9852 | 0.33543 | 0.16386 | 1.2563 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 1134.3723 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 116.3723 | 4.5384 | 0.42102 | 0.20108 | 1.5416 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 1138.1223 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 120.1223 | 4.2506 | 0.35777 | 0.16721 | 1.282 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 1141.8723 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 123.8723 | 4.8309 | 0.44815 | 0.20515 | 1.5728 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 1145.6223 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 127.6223 | 4.5159 | 0.38011 | 0.17056 | 1.3077 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 1149.3723 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 131.3723 | 5.1234 | 0.47529 | 0.20922 | 1.604 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 1153.1223 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 135.1223 | 4.7813 | 0.40244 | 0.17391 | 1.3333 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 1156.8723 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 138.8723 | 5.4159 | 0.50242 | 0.21329 | 1.6352 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 1160.6223 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 142.6223 | 5.0467 | 0.42478 | 0.17727 | 1.359 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 1164.3723 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 146.3723 | 5.7084 | 0.52955 | 0.21736 | 1.6664 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 1168.1223 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 150.1223 | 5.3121 | 0.44712 | 0.18062 | 1.3847 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 1171.8723 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 153.8723 | 6.0009 | 0.55669 | 0.22143 | 1.6976 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 1175.6223 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 157.6223 | 5.5775 | 0.46946 | 0.18397 | 1.4104 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 1179.3723 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 161.3723 | 6.2934 | 0.58382 | 0.2255 | 1.7288 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 1183.1223 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 165.1223 | 5.8429 | 0.4918 | 0.18732 | 1.4361 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 1186.8723 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 168.8723 | 6.5859 | 0.61095 | 0.22957 | 1.76 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMT2 | HI | 1196.0723 | 0.3 | -0.13006 | 61.2584 | 6.5454 | 0.40096 | 178.0723 | 4.5859 | 0.28093 | 0.10228 | 0.78417 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMT2 | HI | 1204.3723 | 0.3 | 0.13944 | 65.6748 | 7.0173 | 0.46086 | 186.3723 | 5.1457 | 0.33794 | 0.11982 | 0.91862 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA3 | HI | 1211.7723 | 0.3 | -0.12488 | 58.8168 | 6.2845 | 0.36964 | 193.7723 | 4.7913 | 0.28181 | 0.097717 | 0.74916 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA3 | HI | 1222.8723 | 0.3 | 0.10723 | 50.5027 | 5.3962 | 0.27252 | 204.8723 | 4.3497 | 0.21967 | 0.073829 | 0.56602 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA2 | HI | 1234.4243 | 0.3 | -0.1468 | 69.1418 | 7.3878 | 0.5108 | 216.4243 | 6.2909 | 0.43496 | 0.14186 | 1.0876 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA2 | HI | 1244.9543 | 0.3 | 0.16713 | 78.7149 | 8.4106 | 0.66204 | 226.9543 | 7.5103 | 0.59117 | 0.18798 | 1.4412 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMT1 | HI | 1258.4543 | 0.3 | -0.18947 | 89.2401 | 9.5352 | 0.85093 | 240.4543 | 9.021 | 0.80504 | 0.24839 | 1.9044 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMT1 | HI | 1261.4043 | 0.3 | 0.16088 | 75.773 | 8.0963 | 0.61348 | 243.4043 | 7.7537 | 0.58752 | 0.18015 | 1.3811 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA1 | LO | 1272.7143 | 0.3 | 0.099551 | 6.7923 | 16.7711 | 0.11391 | 254.7143 | 0.72733 | 0.0049403 | 0.017828 | 0.13668 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA1 | LO | 1276.6143 | 0.3 | -0.079158 | 5.4009 | 13.3356 | 0.072024 | 258.6143 | 0.5872 | 0.0031714 | 0.011279 | 0.086475 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1293.2143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 275.2143 | 0.6796 | 0.0039918 | 0.013377 | 0.10256 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1297.1143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 279.1143 | 0.68522 | 0.0040014 | 0.01323 | 0.10143 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1311.6143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 293.6143 | 0.72082 | 0.0042093 | 0.013261 | 0.10167 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1315.5143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 297.5143 | 0.73466 | 0.0043152 | 0.013425 | 0.10293 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1332.1143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 314.1143 | 0.77565 | 0.004556 | 0.013462 | 0.10321 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1336.0143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 318.0143 | 0.78072 | 0.0045591 | 0.013314 | 0.10207 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1350.5143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 332.5143 | 0.81632 | 0.004767 | 0.013345 | 0.10231 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1354.4143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 336.4143 | 0.83072 | 0.0048795 | 0.01351 | 0.10358 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1371.0143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 353.0143 | 0.87171 | 0.0051202 | 0.013546 | 0.10385 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1374.9143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 356.9143 | 0.87622 | 0.0051168 | 0.013398 | 0.10271 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1389.4143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 371.4143 | 0.91181 | 0.0053246 | 0.013429 | 0.10295 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1393.3143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 375.3143 | 0.92678 | 0.0054437 | 0.013595 | 0.10423 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1409.9143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 391.9143 | 0.96777 | 0.0056844 | 0.013631 | 0.1045 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1413.8143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 395.8143 | 0.97172 | 0.0056744 | 0.013481 | 0.10336 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1428.3143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 410.3143 | 1.0073 | 0.0058823 | 0.013512 | 0.10359 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1432.2143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 414.2143 | 1.0228 | 0.0060079 | 0.013679 | 0.10488 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1448.8143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 430.8143 | 1.0638 | 0.0062487 | 0.013715 | 0.10515 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1452.7143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 434.7143 | 1.0672 | 0.0062321 | 0.013565 | 0.104 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1467.2143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 449.2143 | 1.1028 | 0.00644 | 0.013596 | 0.10424 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1471.1143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 453.1143 | 1.1189 | 0.0065721 | 0.013764 | 0.10552 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1487.7143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 469.7143 | 1.1599 | 0.0068129 | 0.0138 | 0.1058 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1491.6143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 473.6143 | 1.1627 | 0.0067898 | 0.013648 | 0.10464 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1506.1143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 488.1143 | 1.1983 | 0.0069977 | 0.01368 | 0.10488 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1510.0143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 492.0143 | 1.2149 | 0.0071363 | 0.013849 | 0.10617 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1526.6143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 508.6143 | 1.2559 | 0.0073771 | 0.013885 | 0.10645 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1530.5143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 512.5143 | 1.2582 | 0.0073475 | 0.013732 | 0.10528 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1545.0143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 527.0143 | 1.2938 | 0.0075553 | 0.013763 | 0.10552 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1548.9143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 530.9143 | 1.311 | 0.0077005 | 0.013933 | 0.10682 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1565.5143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 547.5143 | 1.352 | 0.0079413 | 0.013969 | 0.1071 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1569.4143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 551.4143 | 1.3537 | 0.0079051 | 0.013816 | 0.10592 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1583.9143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 565.9143 | 1.3893 | 0.008113 | 0.013847 | 0.10616 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1587.8143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 569.8143 | 1.4071 | 0.0082648 | 0.014018 | 0.10747 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1604.4143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 586.4143 | 1.4481 | 0.0085055 | 0.014054 | 0.10775 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1608.3143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 590.3143 | 1.4492 | 0.0084628 | 0.013899 | 0.10656 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1622.8143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 604.8143 | 1.4848 | 0.0086707 | 0.013931 | 0.1068 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1626.7143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 608.7143 | 1.5031 | 0.008829 | 0.014103 | 0.10812 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1643.3143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 625.3143 | 1.5441 | 0.0090698 | 0.014139 | 0.1084 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1647.2143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 629.2143 | 1.5447 | 0.0090205 | 0.013983 | 0.1072 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1661.7143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 643.7143 | 1.5803 | 0.0092284 | 0.014014 | 0.10744 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1665.6143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 647.6143 | 1.5992 | 0.0093932 | 0.014187 | 0.10877 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1682.2143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 651.7857 | 1.6095 | 0.0094537 | 0.014196 | 0.10884 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1686.1143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 647.8857 | 1.5905 | 0.0092882 | 0.014023 | 0.10751 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1700.6143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 633.3857 | 1.5549 | 0.0090803 | 0.013992 | 0.10727 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1704.5143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 629.4857 | 1.5544 | 0.0091303 | 0.014148 | 0.10847 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1721.1143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 612.8857 | 1.5134 | 0.0088895 | 0.014112 | 0.10819 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1725.0143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 608.9857 | 1.495 | 0.0087305 | 0.01394 | 0.10687 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1739.5143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 594.4857 | 1.4594 | 0.0085226 | 0.013908 | 0.10663 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1743.4143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 590.5857 | 1.4584 | 0.008566 | 0.014063 | 0.10782 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1760.0143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 573.9857 | 1.4174 | 0.0083253 | 0.014027 | 0.10754 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1763.9143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 570.0857 | 1.3995 | 0.0081728 | 0.013856 | 0.10623 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1778.4143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 555.5857 | 1.364 | 0.0079649 | 0.013825 | 0.10599 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1782.3143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 551.6857 | 1.3623 | 0.0080018 | 0.013978 | 0.10717 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1798.9143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 535.0857 | 1.3213 | 0.007761 | 0.013942 | 0.10689 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1802.8143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 531.1857 | 1.304 | 0.0076151 | 0.013772 | 0.10559 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1817.3143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 516.6857 | 1.2685 | 0.0074073 | 0.013741 | 0.10535 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1821.2143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 512.7857 | 1.2662 | 0.0074376 | 0.013894 | 0.10652 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1837.8143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 496.1857 | 1.2252 | 0.0071968 | 0.013858 | 0.10624 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1841.7143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 492.2857 | 1.2086 | 0.0070575 | 0.013689 | 0.10495 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1856.2143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 477.7857 | 1.173 | 0.0068496 | 0.013657 | 0.10471 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1860.1143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 473.8857 | 1.1702 | 0.0068734 | 0.013809 | 0.10587 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1876.7143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 457.2857 | 1.1292 | 0.0066326 | 0.013773 | 0.10559 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1880.6143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 453.3857 | 1.1131 | 0.0064998 | 0.013605 | 0.1043 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1895.1143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 438.8857 | 1.0775 | 0.0062919 | 0.013574 | 0.10407 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1899.0143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 434.9857 | 1.0741 | 0.0063092 | 0.013725 | 0.10522 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1915.6143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 418.3857 | 1.0331 | 0.0060684 | 0.013688 | 0.10494 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1919.5143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 414.4857 | 1.0176 | 0.0059421 | 0.013521 | 0.10366 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1934.0143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 399.9857 | 0.98196 | 0.0057342 | 0.01349 | 0.10342 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1937.9143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 396.0857 | 0.97807 | 0.0057449 | 0.01364 | 0.10457 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1954.5143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 379.4857 | 0.93708 | 0.0055042 | 0.013604 | 0.1043 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1958.4143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 375.5857 | 0.92205 | 0.0053844 | 0.013438 | 0.10302 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1972.9143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 361.0857 | 0.88646 | 0.0051766 | 0.013406 | 0.10278 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1976.8143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 357.1857 | 0.88201 | 0.0051807 | 0.013555 | 0.10392 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 1993.4143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 340.5857 | 0.84102 | 0.00494 | 0.013519 | 0.10365 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 1997.3143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 336.6857 | 0.82656 | 0.0048268 | 0.013354 | 0.10238 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2011.8143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 322.1857 | 0.79096 | 0.0046189 | 0.013323 | 0.10214 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2015.7143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 318.2857 | 0.78595 | 0.0046165 | 0.013471 | 0.10328 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2032.3143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 301.6857 | 0.74496 | 0.0043757 | 0.013435 | 0.103 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2036.2143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 297.7857 | 0.73106 | 0.0042691 | 0.01327 | 0.10174 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2050.7143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 283.2857 | 0.69546 | 0.0040612 | 0.013239 | 0.1015 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2054.6143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 279.3857 | 0.6899 | 0.0040523 | 0.013386 | 0.10263 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA1 | LO | 2071.2143 | 0.3 | -0.079158 | 5.4009 | 13.3356 | 0.072024 | 262.7857 | 0.59667 | 0.0032225 | 0.011287 | 0.086534 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA1 | LO | 2075.1143 | 0.3 | 0.099551 | 6.7923 | 16.7711 | 0.11391 | 258.8857 | 0.73924 | 0.0050212 | 0.01784 | 0.13678 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMT1 | HI | 2086.4243 | 0.3 | 0.16088 | 75.773 | 8.0963 | 0.61348 | 247.5757 | 7.8865 | 0.59759 | 0.18166 | 1.3927 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMT1 | HI | 2089.3743 | 0.3 | -0.18947 | 89.2401 | 9.5352 | 0.85093 | 244.6257 | 9.1775 | 0.819 | 0.25049 | 1.9204 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA2 | HI | 2102.8743 | 0.3 | 0.16713 | 78.7149 | 8.4106 | 0.66204 | 231.1257 | 7.6484 | 0.60204 | 0.18961 | 1.4537 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA2 | HI | 2113.4043 | 0.3 | -0.1468 | 69.1418 | 7.3878 | 0.5108 | 220.5957 | 6.4121 | 0.44335 | 0.14312 | 1.0973 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA3 | HI | 2124.9563 | 0.3 | 0.10723 | 50.5027 | 5.3962 | 0.27252 | 209.0437 | 4.4383 | 0.22415 | 0.0745 | 0.57117 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA3 | HI | 2136.0563 | 0.3 | -0.12488 | 58.8168 | 6.2845 | 0.36964 | 197.9437 | 4.8945 | 0.28788 | 0.098627 | 0.75614 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMT2 | HI | 2143.4563 | 0.3 | 0.13944 | 65.6748 | 7.0173 | 0.46086 | 190.5437 | 5.2609 | 0.34551 | 0.12096 | 0.92732 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMT2 | HI | 2151.7563 | 0.3 | -0.13006 | 61.2584 | 6.5454 | 0.40096 | 182.2437 | 4.6933 | 0.28751 | 0.10327 | 0.79174 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 2160.9563 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 173.0437 | 6.7486 | 0.62605 | 0.23183 | 1.7774 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDRF | HI | 2164.7163 | 0.3 | -0.19873 | 93.5985 | 10.0009 | 0.93607 | 169.2837 | 6.6611 | 0.62347 | 0.23393 | 1.7935 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFRF | HI | 2168.4763 | 0.3 | 0.21047 | 99.1305 | 10.592 | 1.05 | 165.5237 | 6.8981 | 0.68381 | 0.26007 | 1.9939 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDRF | HI | 2172.2363 | 0.3 | -0.19873 | 93.5985 | 10.0009 | 0.93607 | 161.7637 | 6.3652 | 0.59578 | 0.22978 | 1.7616 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 2175.9963 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 158.0037 | 6.162 | 0.57163 | 0.22367 | 1.7148 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 2179.7463 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 154.2537 | 5.4583 | 0.45942 | 0.18246 | 1.3989 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 2183.4963 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 150.5037 | 5.8695 | 0.5445 | 0.2196 | 1.6836 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 2187.2463 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 146.7537 | 5.1929 | 0.43709 | 0.17911 | 1.3732 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 2190.9963 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 143.0037 | 5.577 | 0.51737 | 0.21553 | 1.6524 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 2194.7463 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 139.2537 | 4.9275 | 0.41475 | 0.17576 | 1.3475 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 2198.4963 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 135.5037 | 5.2846 | 0.49023 | 0.21146 | 1.6212 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 2202.2463 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 131.7537 | 4.6621 | 0.39241 | 0.17241 | 1.3218 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 2205.9963 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 128.0037 | 4.9921 | 0.4631 | 0.20739 | 1.59 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 2209.7463 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 124.2537 | 4.3967 | 0.37007 | 0.16906 | 1.2961 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 2213.4963 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 120.5037 | 4.6996 | 0.43596 | 0.20332 | 1.5588 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 2217.2463 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 116.7537 | 4.1314 | 0.34774 | 0.16571 | 1.2704 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 2220.9963 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 113.0037 | 4.4071 | 0.40883 | 0.19925 | 1.5276 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 2224.7463 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 109.2537 | 3.866 | 0.3254 | 0.16236 | 1.2447 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 2228.4963 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 105.5037 | 4.1146 | 0.3817 | 0.19518 | 1.4964 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 2232.2463 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 101.7537 | 3.6006 | 0.30306 | 0.15901 | 1.2191 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 2235.9963 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 98.0037 | 3.8221 | 0.35456 | 0.19111 | 1.4652 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 2239.7463 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 94.2537 | 3.3352 | 0.28072 | 0.15566 | 1.1934 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 2243.4963 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 90.5037 | 3.5296 | 0.32743 | 0.18704 | 1.434 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 2247.2463 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 86.7537 | 3.0698 | 0.25838 | 0.15231 | 1.1677 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 2250.9963 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 83.0037 | 3.2371 | 0.30029 | 0.18297 | 1.4028 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMT2 | HI | 2260.1963 | 0.3 | -0.13006 | 61.2584 | 6.5454 | 0.40096 | 73.8037 | 1.9007 | 0.11643 | 0.077609 | 0.595 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMT2 | HI | 2268.4963 | 0.3 | 0.13944 | 65.6748 | 7.0173 | 0.46086 | 65.5037 | 1.8085 | 0.11878 | 0.086945 | 0.66658 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA3 | HI | 2275.8963 | 0.3 | -0.12488 | 58.8168 | 6.2845 | 0.36964 | 58.1037 | 1.4367 | 0.084503 | 0.068121 | 0.52226 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA3 | HI | 2286.9963 | 0.3 | 0.10723 | 50.5027 | 5.3962 | 0.27252 | 47.0037 | 0.99795 | 0.050399 | 0.048438 | 0.37136 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA2 | HI | 2298.5483 | 0.3 | -0.1468 | 69.1418 | 7.3878 | 0.5108 | 35.4517 | 1.0305 | 0.071249 | 0.087308 | 0.66936 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA2 | HI | 2309.0783 | 0.3 | 0.16713 | 78.7149 | 8.4106 | 0.66204 | 24.9217 | 0.8247 | 0.064916 | 0.10904 | 0.836 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMT1 | HI | 2322.5783 | 0.3 | -0.18947 | 89.2401 | 9.5352 | 0.85093 | 11.4217 | 0.4285 | 0.03824 | 0.13337 | 1.0225 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMT1 | HI | 2325.5283 | 0.3 | 0.16088 | 75.773 | 8.0963 | 0.61348 | 8.4717 | 0.26987 | 0.020448 | 0.095089 | 0.72902 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA1 | LO | 2336.8383 | 0.3 | 0.099551 | 6.7923 | 16.7711 | 0.11391 | 2.8383 | 0.0081049 | 5.5051e-05 | 0.017095 | 0.13106 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA1 | LO | 2340.7383 | 0.3 | -0.079158 | 5.4009 | 13.3356 | 0.072024 | 6.7383 | 0.0153 | 8.2633e-05 | 0.010816 | 0.082923 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2357.3383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 23.3383 | 0.05763 | 0.00033851 | 0.012829 | 0.098355 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2361.2383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 27.2383 | 0.06687 | 0.00039049 | 0.012689 | 0.097279 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2375.7383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 41.7383 | 0.10247 | 0.00059837 | 0.01272 | 0.097518 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2379.6383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 45.6383 | 0.1127 | 0.00066195 | 0.012877 | 0.098727 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2396.2383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 62.2383 | 0.15369 | 0.00090272 | 0.012914 | 0.099004 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2400.1383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 66.1383 | 0.16237 | 0.00094817 | 0.012772 | 0.09792 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2414.6383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 80.6383 | 0.19797 | 0.001156 | 0.012803 | 0.098159 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2418.5383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 84.5383 | 0.20875 | 0.0012262 | 0.012962 | 0.099376 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2435.1383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 101.1383 | 0.24974 | 0.0014669 | 0.012998 | 0.099653 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2439.0383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 105.0383 | 0.25787 | 0.0015058 | 0.012856 | 0.098562 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2453.5383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 119.5383 | 0.29346 | 0.0017137 | 0.012887 | 0.098801 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2457.4383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 123.4383 | 0.30481 | 0.0017904 | 0.013047 | 0.10003 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2474.0383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 140.0383 | 0.3458 | 0.0020312 | 0.013083 | 0.1003 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2477.9383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 143.9383 | 0.35337 | 0.0020635 | 0.01294 | 0.099203 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2492.4383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 158.4383 | 0.38896 | 0.0022714 | 0.012971 | 0.099442 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2496.3383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 162.3383 | 0.40087 | 0.0023546 | 0.013131 | 0.10067 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2512.9383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 178.9383 | 0.44186 | 0.0025954 | 0.013167 | 0.10095 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2516.8383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 182.8383 | 0.44886 | 0.0026212 | 0.013023 | 0.099844 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2531.3383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 197.3383 | 0.48446 | 0.0028291 | 0.013054 | 0.10008 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2535.2383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 201.2383 | 0.49693 | 0.0029188 | 0.013216 | 0.10132 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2551.8383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 217.8383 | 0.53792 | 0.0031596 | 0.013252 | 0.1016 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2555.7383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 221.7383 | 0.54436 | 0.0031789 | 0.013107 | 0.10049 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2570.2383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 236.2383 | 0.57996 | 0.0033867 | 0.013138 | 0.10072 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2574.1383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 240.1383 | 0.59298 | 0.003483 | 0.013301 | 0.10197 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2590.7383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 256.7383 | 0.63397 | 0.0037238 | 0.013337 | 0.10225 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2594.6383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 260.6383 | 0.63986 | 0.0037365 | 0.01319 | 0.10113 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2609.1383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 275.1383 | 0.67546 | 0.0039444 | 0.013222 | 0.10137 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2613.0383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 279.0383 | 0.68904 | 0.0040473 | 0.013385 | 0.10262 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2629.6383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 295.6383 | 0.73003 | 0.004288 | 0.013421 | 0.1029 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2633.5383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 299.5383 | 0.73536 | 0.0042942 | 0.013274 | 0.10177 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2648.0383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 314.0383 | 0.77096 | 0.0045021 | 0.013305 | 0.10201 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2651.9383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 317.9383 | 0.7851 | 0.0046115 | 0.01347 | 0.10327 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2668.5383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 334.5383 | 0.82609 | 0.0048522 | 0.013506 | 0.10355 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2672.4383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 338.4383 | 0.83086 | 0.0048519 | 0.013358 | 0.10241 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2686.9383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 352.9383 | 0.86646 | 0.0050598 | 0.013389 | 0.10265 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2690.8383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 356.8383 | 0.88115 | 0.0051757 | 0.013555 | 0.10392 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2707.4383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 373.4383 | 0.92215 | 0.0054165 | 0.013591 | 0.1042 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2711.3383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 377.3383 | 0.92636 | 0.0054096 | 0.013441 | 0.10305 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2725.8383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 391.8383 | 0.96195 | 0.0056174 | 0.013473 | 0.10329 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2729.7383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 395.7383 | 0.97721 | 0.0057399 | 0.013639 | 0.10457 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2746.3383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 412.3383 | 1.0182 | 0.0059807 | 0.013675 | 0.10484 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2750.2383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 416.2383 | 1.0219 | 0.0059672 | 0.013525 | 0.10369 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2764.7383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 430.7383 | 1.0575 | 0.0061751 | 0.013556 | 0.10393 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2768.6383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 434.6383 | 1.0733 | 0.0063041 | 0.013724 | 0.10522 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2785.2383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 451.2383 | 1.1143 | 0.0065449 | 0.01376 | 0.10549 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2789.1383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 455.1383 | 1.1174 | 0.0065249 | 0.013609 | 0.10433 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2803.6383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 469.6383 | 1.153 | 0.0067328 | 0.01364 | 0.10457 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2807.5383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 473.5383 | 1.1693 | 0.0068683 | 0.013808 | 0.10586 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2824.1383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 490.1383 | 1.2103 | 0.0071091 | 0.013845 | 0.10614 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2828.0383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 494.0383 | 1.2129 | 0.0070826 | 0.013692 | 0.10497 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2842.5383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 508.5383 | 1.2485 | 0.0072905 | 0.013724 | 0.10521 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2846.4383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 512.4383 | 1.2654 | 0.0074326 | 0.013893 | 0.10651 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2863.0383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 529.0383 | 1.3064 | 0.0076733 | 0.013929 | 0.10679 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2866.9383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 532.9383 | 1.3084 | 0.0076403 | 0.013776 | 0.10562 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2881.4383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 547.4383 | 1.3439 | 0.0078481 | 0.013807 | 0.10586 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2885.3383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 551.3383 | 1.3614 | 0.0079968 | 0.013978 | 0.10716 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2901.9383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 567.9383 | 1.4024 | 0.0082376 | 0.014014 | 0.10744 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2905.8383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 571.8383 | 1.4039 | 0.0081979 | 0.01386 | 0.10626 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2920.3383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 586.3383 | 1.4394 | 0.0084058 | 0.013891 | 0.1065 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2924.2383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 590.2383 | 1.4575 | 0.008561 | 0.014062 | 0.10781 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2940.8383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 606.8383 | 1.4985 | 0.0088018 | 0.014098 | 0.10809 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2944.7383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 610.7383 | 1.4993 | 0.0087556 | 0.013943 | 0.1069 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2959.2383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 625.2383 | 1.5349 | 0.0089635 | 0.013975 | 0.10714 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2963.1383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 629.1383 | 1.5536 | 0.0091252 | 0.014147 | 0.10846 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 2979.7383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 645.7383 | 1.5945 | 0.009366 | 0.014183 | 0.10874 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2983.6383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 649.6383 | 1.5948 | 0.0093133 | 0.014027 | 0.10754 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 2998.1383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 664.1383 | 1.6304 | 0.0095212 | 0.014058 | 0.10778 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3002.0383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 668.0383 | 1.6496 | 0.0096894 | 0.014232 | 0.10911 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3018.6383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 684.6383 | 1.6906 | 0.0099302 | 0.014268 | 0.10939 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3022.5383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 688.5383 | 1.6903 | 0.009871 | 0.014111 | 0.10818 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3037.0383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 703.0383 | 1.7259 | 0.010079 | 0.014142 | 0.10842 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3040.9383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 706.9383 | 1.7457 | 0.010254 | 0.014316 | 0.10976 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3057.5383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 723.5383 | 1.7867 | 0.010494 | 0.014352 | 0.11003 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3061.4383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 727.4383 | 1.7858 | 0.010429 | 0.014194 | 0.10882 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3075.9383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 741.9383 | 1.8214 | 0.010637 | 0.014225 | 0.10906 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3079.8383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 745.8383 | 1.8417 | 0.010818 | 0.014401 | 0.11041 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3096.4383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 762.4383 | 1.8827 | 0.011059 | 0.014437 | 0.11068 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3100.3383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 766.3383 | 1.8813 | 0.010986 | 0.014278 | 0.10946 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3114.8383 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 780.8383 | 1.9169 | 0.011194 | 0.014309 | 0.1097 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3118.7383 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 784.7383 | 1.9378 | 0.011382 | 0.014485 | 0.11106 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA1 | LO | 3135.3383 | 0.3 | -0.079158 | 5.4009 | 13.3356 | 0.072024 | 801.3383 | 1.8195 | 0.0098268 | 0.012278 | 0.094129 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA1 | LO | 3139.2383 | 0.3 | 0.099551 | 6.7923 | 16.7711 | 0.11391 | 805.2383 | 2.2993 | 0.015618 | 0.01943 | 0.14896 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMINJ1 | LO | 3150.0483 | 0.3 | 0.076118 | 5.1935 | 12.8234 | 0.066599 | 816.0483 | 1.7817 | 0.0092534 | 0.011378 | 0.08723 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMINJ1 | HI | 3151.3483 | 0.3 | -0.12291 | 57.8873 | 6.1852 | 0.35805 | 817.3483 | 19.8909 | 1.1514 | 0.22642 | 1.7359 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMINJ2 | LO | 3167.3333 | 0.3 | 0.072346 | 4.9361 | 12.1879 | 0.060161 | 833.3333 | 1.7293 | 0.0085359 | 0.010304 | 0.079001 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMINJ2 | LO | 3173.5173 | 0.3 | -0.099764 | 6.8068 | 16.807 | 0.1144 | 839.5173 | 2.4024 | 0.016352 | 0.019613 | 0.15037 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMINJ3 | LO | 3185.3387 | 0.3 | 0.064087 | 4.3726 | 10.7965 | 0.047209 | 851.3387 | 1.565 | 0.006843 | 0.0081078 | 0.06216 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMINJ3 | LO | 3200.1387 | 0.3 | -0.080568 | 5.4971 | 13.5731 | 0.074613 | 866.1387 | 2.0016 | 0.011003 | 0.012842 | 0.098458 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
QFMINJ3 | LO | 3214.9387 | 0.3 | 0.064087 | 4.3726 | 10.7965 | 0.047209 | 880.9387 | 1.6194 | 0.0070809 | 0.0081435 | 0.062433 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMINJ3 | LO | 3229.7387 | 0.3 | -0.080568 | 5.4971 | 13.5731 | 0.074613 | 895.7387 | 2.07 | 0.011379 | 0.012899 | 0.098891 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
QFMINJ3 | LO | 3244.5387 | 0.3 | 0.064087 | 4.3726 | 10.7965 | 0.047209 | 910.5387 | 1.6738 | 0.0073188 | 0.0081791 | 0.062707 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMINJ3 | LO | 3259.3387 | 0.3 | -0.080568 | 5.4971 | 13.5731 | 0.074613 | 925.3387 | 2.1384 | 0.011755 | 0.012955 | 0.099323 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
QFINJ4H | HI | 3274.1387 | 0.3 | 0.083398 | 39.2796 | 4.197 | 0.16486 | 940.1387 | 15.5247 | 0.6098 | 0.1162 | 0.89086 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
QDINJ2 | HI | 3288.7887 | 0.3 | -0.11648 | 54.862 | 5.862 | 0.3216 | 954.7887 | 22.0213 | 1.2081 | 0.22946 | 1.7592 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
QFINJ3 | HI | 3295.4407 | 0.3 | 0.091096 | 42.9055 | 4.5844 | 0.1967 | 961.4407 | 17.342 | 0.74407 | 0.14111 | 1.0819 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
QFINJ1 | HI | 3306.0207 | 0.3 | 0.16853 | 79.3772 | 8.4814 | 0.67323 | 972.0207 | 32.4366 | 2.5747 | 0.48719 | 3.7351 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
QDINJ1 | HI | 3309.9297 | 0.3 | -0.21745 | 102.4191 | 10.9434 | 1.1208 | 975.9297 | 42.0207 | 4.3037 | 0.81368 | 6.2382 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
QFINJ2H | HI | 3313.6977 | 0.3 | 0.28175 | 132.7032 | 14.1792 | 1.8816 | 979.6977 | 54.656 | 7.253 | 1.3702 | 10.5049 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
QDINJ1 | HI | 3317.4657 | 0.3 | -0.21745 | 102.4191 | 10.9434 | 1.1208 | 983.4657 | 42.3452 | 4.337 | 0.81867 | 6.2764 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
QFINJ1 | HI | 3321.3747 | 0.3 | 0.16853 | 79.3772 | 8.4814 | 0.67323 | 987.3747 | 32.949 | 2.6154 | 0.49329 | 3.7819 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
QFINJ1 | HI | 3328.6747 | 0.3 | 0.16853 | 79.3772 | 8.4814 | 0.67323 | 994.6747 | 33.1926 | 2.6347 | 0.49619 | 3.8042 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
QDINJ1 | HI | 3332.5837 | 0.3 | -0.21745 | 102.4191 | 10.9434 | 1.1208 | 998.5837 | 42.9961 | 4.4036 | 0.82867 | 6.3531 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
QFINJ2H | HI | 3336.3517 | 0.3 | 0.28175 | 132.7032 | 14.1792 | 1.8816 | 1002.3517 | 55.9198 | 7.4207 | 1.3954 | 10.6977 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
QDINJ1 | HI | 3340.1197 | 0.3 | -0.21745 | 102.4191 | 10.9434 | 1.1208 | 1006.1197 | 43.3206 | 4.4369 | 0.83365 | 6.3913 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
QFINJ1 | HI | 3344.0287 | 0.3 | 0.16853 | 79.3772 | 8.4814 | 0.67323 | 1010.0287 | 33.7049 | 2.6754 | 0.50229 | 3.8509 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
QFINJ1 | HI | 3351.3287 | 0.3 | 0.16853 | 79.3772 | 8.4814 | 0.67323 | 1017.3287 | 33.9485 | 2.6947 | 0.5052 | 3.8732 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
QDINJ1 | HI | 3355.2377 | 0.3 | -0.21745 | 102.4191 | 10.9434 | 1.1208 | 1014.7623 | 43.6927 | 4.475 | 0.83937 | 6.4352 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
QFINJ2H | HI | 3359.0057 | 0.3 | 0.28175 | 132.7032 | 14.1792 | 1.8816 | 1010.9943 | 56.402 | 7.4847 | 1.405 | 10.7713 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
QDINJ1 | HI | 3362.7737 | 0.3 | -0.21745 | 102.4191 | 10.9434 | 1.1208 | 1007.2263 | 43.3683 | 4.4417 | 0.83438 | 6.3969 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
QFINJ1 | HI | 3366.6827 | 0.3 | 0.16853 | 79.3772 | 8.4814 | 0.67323 | 1003.3173 | 33.481 | 2.6576 | 0.49963 | 3.8305 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
QFINJ1 | HI | 3373.9827 | 0.3 | 0.16853 | 79.3772 | 8.4814 | 0.67323 | 996.0173 | 33.2374 | 2.6383 | 0.49673 | 3.8082 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
QDINJ1 | HI | 3377.8917 | 0.3 | -0.21745 | 102.4191 | 10.9434 | 1.1208 | 992.1083 | 42.7173 | 4.3751 | 0.82438 | 6.3203 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
QFINJ2H | HI | 3381.6597 | 0.3 | 0.28175 | 132.7032 | 14.1792 | 1.8816 | 988.3403 | 55.1381 | 7.317 | 1.3798 | 10.5784 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
QDINJ1 | HI | 3385.4277 | 0.3 | -0.21745 | 102.4191 | 10.9434 | 1.1208 | 984.5723 | 42.3928 | 4.3418 | 0.8194 | 6.282 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
QFINJ1 | HI | 3389.3367 | 0.3 | 0.16853 | 79.3772 | 8.4814 | 0.67323 | 980.6633 | 32.725 | 2.5976 | 0.49063 | 3.7615 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
QFINJ3 | HI | 3399.9167 | 0.3 | 0.091096 | 42.9055 | 4.5844 | 0.1967 | 970.0833 | 17.4979 | 0.75076 | 0.14212 | 1.0896 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
QDINJ2 | HI | 3406.5687 | 0.3 | -0.11648 | 54.862 | 5.862 | 0.3216 | 963.4313 | 22.2206 | 1.2191 | 0.2311 | 1.7718 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
QFINJ4H | HI | 3421.2187 | 0.3 | 0.083398 | 39.2796 | 4.197 | 0.16486 | 948.7813 | 15.6674 | 0.61541 | 0.11704 | 0.89731 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
QDMINJ3 | LO | 3436.0187 | 0.3 | -0.080568 | 5.4971 | 13.5731 | 0.074613 | 933.9813 | 2.1584 | 0.011865 | 0.012972 | 0.099449 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
QFMINJ3 | LO | 3450.8187 | 0.3 | 0.064087 | 4.3726 | 10.7965 | 0.047209 | 919.1813 | 1.6897 | 0.0073883 | 0.0081896 | 0.062787 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMINJ3 | LO | 3465.6187 | 0.3 | -0.080568 | 5.4971 | 13.5731 | 0.074613 | 904.3813 | 2.09 | 0.011489 | 0.012915 | 0.099017 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
QFMINJ3 | LO | 3480.4187 | 0.3 | 0.064087 | 4.3726 | 10.7965 | 0.047209 | 889.5813 | 1.6353 | 0.0071504 | 0.0081539 | 0.062513 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMINJ3 | LO | 3495.2187 | 0.3 | -0.080568 | 5.4971 | 13.5731 | 0.074613 | 874.7813 | 2.0216 | 0.011113 | 0.012859 | 0.098585 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
QFMINJ3 | LO | 3510.0187 | 0.3 | 0.064087 | 4.3726 | 10.7965 | 0.047209 | 859.9813 | 1.5809 | 0.0069124 | 0.0081182 | 0.062239 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMINJ2 | LO | 3521.84 | 0.3 | -0.099764 | 6.8068 | 16.807 | 0.1144 | 848.16 | 2.4271 | 0.016521 | 0.019638 | 0.15056 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMINJ2 | LO | 3528.024 | 0.3 | 0.072346 | 4.9361 | 12.1879 | 0.060161 | 841.976 | 1.7472 | 0.0086244 | 0.010318 | 0.079103 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMINJ1 | HI | 3544.009 | 0.3 | -0.12291 | 57.8873 | 6.1852 | 0.35805 | 825.991 | 20.1012 | 1.1636 | 0.22825 | 1.7499 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMINJ1 | LO | 3545.309 | 0.3 | 0.076118 | 5.1935 | 12.8234 | 0.066599 | 824.691 | 1.8006 | 0.0093514 | 0.011392 | 0.087342 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA1 | LO | 3556.119 | 0.3 | 0.099551 | 6.7923 | 16.7711 | 0.11391 | 813.881 | 2.324 | 0.015785 | 0.019455 | 0.14915 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA1 | LO | 3560.019 | 0.3 | -0.079158 | 5.4009 | 13.3356 | 0.072024 | 809.981 | 1.8391 | 0.0099328 | 0.012294 | 0.094251 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3576.619 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 793.381 | 1.9591 | 0.011507 | 0.014504 | 0.1112 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3580.519 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 789.481 | 1.9382 | 0.011318 | 0.014328 | 0.10985 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3595.019 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 774.981 | 1.9026 | 0.01111 | 0.014297 | 0.10961 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3598.919 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 771.081 | 1.9041 | 0.011184 | 0.014456 | 0.11083 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3615.519 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 754.481 | 1.8631 | 0.010943 | 0.01442 | 0.11055 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3619.419 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 750.581 | 1.8427 | 0.01076 | 0.014244 | 0.1092 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3633.919 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 736.081 | 1.8071 | 0.010553 | 0.014213 | 0.10897 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3637.819 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 732.181 | 1.808 | 0.01062 | 0.014371 | 0.11018 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3654.419 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 715.581 | 1.767 | 0.010379 | 0.014335 | 0.1099 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3658.319 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 711.681 | 1.7472 | 0.010203 | 0.01416 | 0.10856 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3672.819 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 697.181 | 1.7116 | 0.0099949 | 0.014129 | 0.10832 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3676.719 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 693.281 | 1.7119 | 0.010056 | 0.014287 | 0.10953 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3693.319 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 676.681 | 1.671 | 0.0098148 | 0.01425 | 0.10925 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3697.219 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 672.781 | 1.6517 | 0.0096451 | 0.014077 | 0.10792 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3711.719 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 658.281 | 1.6161 | 0.0094372 | 0.014046 | 0.10768 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3715.619 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 654.381 | 1.6159 | 0.0094913 | 0.014202 | 0.10888 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3732.219 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 637.781 | 1.5749 | 0.0092506 | 0.014166 | 0.1086 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3736.119 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 633.881 | 1.5562 | 0.0090874 | 0.013993 | 0.10728 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3750.619 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 619.381 | 1.5206 | 0.0088795 | 0.013962 | 0.10704 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3754.519 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 615.481 | 1.5198 | 0.0089271 | 0.014117 | 0.10823 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3771.119 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 598.881 | 1.4788 | 0.0086864 | 0.014081 | 0.10796 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3775.019 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 594.981 | 1.4607 | 0.0085297 | 0.013909 | 0.10664 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3789.519 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 580.481 | 1.4251 | 0.0083218 | 0.013878 | 0.1064 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3793.419 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 576.581 | 1.4238 | 0.0083629 | 0.014033 | 0.10758 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3810.019 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 559.981 | 1.3828 | 0.0081221 | 0.013997 | 0.10731 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3813.919 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 556.081 | 1.3652 | 0.007972 | 0.013826 | 0.106 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3828.419 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 541.581 | 1.3296 | 0.0077642 | 0.013795 | 0.10576 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3832.319 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 537.681 | 1.3277 | 0.0077987 | 0.013948 | 0.10693 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3848.919 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 521.081 | 1.2867 | 0.0075579 | 0.013912 | 0.10666 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3852.819 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 517.181 | 1.2697 | 0.0074144 | 0.013742 | 0.10536 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3867.319 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 502.681 | 1.2341 | 0.0072065 | 0.013711 | 0.10512 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3871.219 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 498.781 | 1.2317 | 0.0072345 | 0.013863 | 0.10629 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3887.819 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 482.181 | 1.1907 | 0.0069937 | 0.013827 | 0.10601 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3891.719 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 478.281 | 1.1742 | 0.0068567 | 0.013659 | 0.10472 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3906.219 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 463.781 | 1.1386 | 0.0066488 | 0.013627 | 0.10448 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3910.119 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 459.881 | 1.1356 | 0.0066703 | 0.013779 | 0.10564 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3926.719 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 443.281 | 1.0946 | 0.0064295 | 0.013743 | 0.10536 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3930.619 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 439.381 | 1.0787 | 0.006299 | 0.013575 | 0.10407 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3945.119 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 424.881 | 1.0431 | 0.0060911 | 0.013544 | 0.10383 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3949.019 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 420.981 | 1.0395 | 0.006106 | 0.013694 | 0.10499 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3965.619 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 404.381 | 0.99855 | 0.0058653 | 0.013658 | 0.10471 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3969.519 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 400.481 | 0.98317 | 0.0057413 | 0.013491 | 0.10343 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 3984.019 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 385.981 | 0.94757 | 0.0055335 | 0.01346 | 0.10319 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 3987.919 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 382.081 | 0.94349 | 0.0055418 | 0.013609 | 0.10434 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4004.519 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 365.481 | 0.9025 | 0.005301 | 0.013573 | 0.10406 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4008.419 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 361.581 | 0.88767 | 0.0051837 | 0.013408 | 0.10279 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4022.919 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 347.081 | 0.85208 | 0.0049758 | 0.013376 | 0.10255 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4026.819 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 343.181 | 0.84743 | 0.0049776 | 0.013525 | 0.10369 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4043.419 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 326.581 | 0.80644 | 0.0047368 | 0.013489 | 0.10341 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4047.319 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 322.681 | 0.79217 | 0.004626 | 0.013324 | 0.10215 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4061.819 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 308.181 | 0.75658 | 0.0044181 | 0.013293 | 0.10191 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4065.719 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 304.281 | 0.75137 | 0.0044134 | 0.01344 | 0.10304 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4082.319 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 287.681 | 0.71038 | 0.0041726 | 0.013404 | 0.10276 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4086.219 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 283.781 | 0.69668 | 0.0040683 | 0.01324 | 0.10151 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4100.719 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 269.281 | 0.66108 | 0.0038604 | 0.013209 | 0.10127 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4104.619 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 265.381 | 0.65532 | 0.0038492 | 0.013356 | 0.10239 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4121.219 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 248.781 | 0.61432 | 0.0036084 | 0.013319 | 0.10212 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4125.119 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 244.881 | 0.60118 | 0.0035106 | 0.013157 | 0.10087 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4139.619 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 230.381 | 0.56558 | 0.0033028 | 0.013125 | 0.10063 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4143.519 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 226.481 | 0.55926 | 0.0032849 | 0.013271 | 0.10174 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4160.119 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 209.881 | 0.51827 | 0.0030442 | 0.013235 | 0.10147 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4164.019 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 205.981 | 0.50568 | 0.002953 | 0.013073 | 0.10023 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4178.519 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 191.481 | 0.47008 | 0.0027451 | 0.013042 | 0.099987 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4182.419 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 187.581 | 0.4632 | 0.0027207 | 0.013186 | 0.10109 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4199.019 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 170.981 | 0.42221 | 0.00248 | 0.01315 | 0.10082 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4202.919 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 167.081 | 0.41018 | 0.0023953 | 0.012989 | 0.099585 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4217.419 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 152.581 | 0.37458 | 0.0021874 | 0.012958 | 0.099346 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4221.319 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 148.681 | 0.36714 | 0.0021565 | 0.013102 | 0.10045 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4237.919 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 132.081 | 0.32615 | 0.0019157 | 0.013066 | 0.10017 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4241.819 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 128.181 | 0.31468 | 0.0018376 | 0.012906 | 0.098943 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4256.319 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 113.681 | 0.27908 | 0.0016297 | 0.012874 | 0.098704 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4260.219 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 109.781 | 0.27109 | 0.0015923 | 0.013017 | 0.099797 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4276.819 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 93.181 | 0.2301 | 0.0013515 | 0.012981 | 0.09952 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4280.719 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 89.281 | 0.21918 | 0.0012799 | 0.012822 | 0.098302 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4295.219 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 74.781 | 0.18359 | 0.0010721 | 0.012791 | 0.098063 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4299.119 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 70.881 | 0.17503 | 0.0010281 | 0.012932 | 0.099148 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4315.719 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 54.281 | 0.13404 | 0.00078731 | 0.012896 | 0.098872 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4319.619 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 50.381 | 0.12368 | 0.00072227 | 0.012738 | 0.097661 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4334.119 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 35.881 | 0.088087 | 0.00051439 | 0.012707 | 0.097422 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4338.019 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 31.981 | 0.078972 | 0.00046386 | 0.012848 | 0.0985 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA1 | LO | 4354.619 | 0.3 | -0.079158 | 5.4009 | 13.3356 | 0.072024 | 15.381 | 0.034923 | 0.00018862 | 0.010832 | 0.083045 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA1 | LO | 4358.519 | 0.3 | 0.099551 | 6.7923 | 16.7711 | 0.11391 | 11.481 | 0.032784 | 0.00022268 | 0.017121 | 0.13126 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMT1 | HI | 4369.829 | 0.3 | 0.16088 | 75.773 | 8.0963 | 0.61348 | 0.17096 | 0.005446 | 0.00041266 | 0.092084 | 0.70598 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMT1 | HI | 4372.779 | 0.3 | -0.18947 | 89.2401 | 9.5352 | 0.85093 | 2.779 | 0.10426 | 0.0093042 | 0.12903 | 0.98926 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA2 | HI | 4386.279 | 0.3 | 0.16713 | 78.7149 | 8.4106 | 0.66204 | 16.279 | 0.5387 | 0.042404 | 0.10567 | 0.81011 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA2 | HI | 4396.809 | 0.3 | -0.1468 | 69.1418 | 7.3878 | 0.5108 | 26.809 | 0.77927 | 0.05388 | 0.084702 | 0.64938 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA3 | HI | 4408.361 | 0.3 | 0.10723 | 50.5027 | 5.3962 | 0.27252 | 38.361 | 0.81446 | 0.041132 | 0.047048 | 0.3607 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA3 | HI | 4419.461 | 0.3 | -0.12488 | 58.8168 | 6.2845 | 0.36964 | 49.461 | 1.223 | 0.071933 | 0.066235 | 0.5078 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMT2 | HI | 4426.861 | 0.3 | 0.13944 | 65.6748 | 7.0173 | 0.46086 | 56.861 | 1.5699 | 0.1031 | 0.084595 | 0.64856 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMT2 | HI | 4435.161 | 0.3 | -0.13006 | 61.2584 | 6.5454 | 0.40096 | 65.161 | 1.6781 | 0.1028 | 0.075564 | 0.57932 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 4444.361 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 74.361 | 2.9 | 0.26903 | 0.17828 | 1.3668 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDRF | HI | 4448.121 | 0.3 | -0.19873 | 93.5985 | 10.0009 | 0.93607 | 78.121 | 3.074 | 0.28772 | 0.18357 | 1.4074 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFRF | HI | 4451.881 | 0.3 | 0.21047 | 99.1305 | 10.592 | 1.05 | 81.881 | 3.4124 | 0.33827 | 0.20824 | 1.5965 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDRF | HI | 4455.641 | 0.3 | -0.19873 | 93.5985 | 10.0009 | 0.93607 | 85.641 | 3.3699 | 0.31542 | 0.18772 | 1.4392 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 4459.401 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 89.401 | 3.4866 | 0.32344 | 0.18644 | 1.4294 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 4463.151 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 93.151 | 3.2962 | 0.27744 | 0.15516 | 1.1896 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 4466.901 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 96.901 | 3.7791 | 0.35057 | 0.19051 | 1.4606 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 4470.651 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 100.651 | 3.5616 | 0.29978 | 0.15851 | 1.2153 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 4474.401 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 104.401 | 4.0716 | 0.37771 | 0.19458 | 1.4918 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 4478.151 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 108.151 | 3.8269 | 0.32211 | 0.16186 | 1.241 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 4481.901 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 111.901 | 4.3641 | 0.40484 | 0.19865 | 1.523 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 4485.651 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 115.651 | 4.0923 | 0.34445 | 0.16522 | 1.2667 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 4489.401 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 119.401 | 4.6566 | 0.43197 | 0.20272 | 1.5542 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 4493.151 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 123.151 | 4.3577 | 0.36679 | 0.16857 | 1.2923 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 4496.901 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 126.901 | 4.9491 | 0.45911 | 0.20679 | 1.5854 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 4500.651 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 130.651 | 4.6231 | 0.38913 | 0.17192 | 1.318 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 4504.401 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 134.401 | 5.2416 | 0.48624 | 0.21086 | 1.6166 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 4508.151 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 138.151 | 4.8885 | 0.41147 | 0.17527 | 1.3437 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 4511.901 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 141.901 | 5.534 | 0.51338 | 0.21493 | 1.6478 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 4515.651 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 145.651 | 5.1539 | 0.4338 | 0.17862 | 1.3694 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 4519.401 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 149.401 | 5.8265 | 0.54051 | 0.219 | 1.679 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 4523.151 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 153.151 | 5.4193 | 0.45614 | 0.18197 | 1.3951 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 4526.901 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 156.901 | 6.119 | 0.56764 | 0.22307 | 1.7102 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 4530.651 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 160.651 | 5.6847 | 0.47848 | 0.18532 | 1.4208 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 4534.401 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 164.401 | 6.4115 | 0.59478 | 0.22714 | 1.7414 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMT2 | HI | 4543.601 | 0.3 | -0.13006 | 61.2584 | 6.5454 | 0.40096 | 173.601 | 4.4708 | 0.27387 | 0.10123 | 0.77606 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMT2 | HI | 4551.901 | 0.3 | 0.13944 | 65.6748 | 7.0173 | 0.46086 | 181.901 | 5.0222 | 0.32984 | 0.1186 | 0.9093 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA3 | HI | 4559.301 | 0.3 | -0.12488 | 58.8168 | 6.2845 | 0.36964 | 189.301 | 4.6808 | 0.27531 | 0.096742 | 0.74169 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA3 | HI | 4570.401 | 0.3 | 0.10723 | 50.5027 | 5.3962 | 0.27252 | 200.401 | 4.2548 | 0.21488 | 0.07311 | 0.56051 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA2 | HI | 4581.953 | 0.3 | -0.1468 | 69.1418 | 7.3878 | 0.5108 | 211.953 | 6.1609 | 0.42598 | 0.14052 | 1.0773 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA2 | HI | 4592.483 | 0.3 | 0.16713 | 78.7149 | 8.4106 | 0.66204 | 222.483 | 7.3624 | 0.57953 | 0.18624 | 1.4278 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMT1 | HI | 4605.983 | 0.3 | -0.18947 | 89.2401 | 9.5352 | 0.85093 | 235.983 | 8.8533 | 0.79007 | 0.24615 | 1.8871 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMT1 | HI | 4608.933 | 0.3 | 0.16088 | 75.773 | 8.0963 | 0.61348 | 238.933 | 7.6112 | 0.57673 | 0.17853 | 1.3687 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA1 | LO | 4620.243 | 0.3 | 0.099551 | 6.7923 | 16.7711 | 0.11391 | 250.243 | 0.71457 | 0.0048535 | 0.017815 | 0.13658 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA1 | LO | 4624.143 | 0.3 | -0.079158 | 5.4009 | 13.3356 | 0.072024 | 254.143 | 0.57704 | 0.0031166 | 0.011271 | 0.086412 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4640.743 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 270.743 | 0.66856 | 0.0039269 | 0.013367 | 0.10248 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4644.643 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 274.643 | 0.67424 | 0.0039373 | 0.013221 | 0.10136 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4659.143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 289.143 | 0.70984 | 0.0041452 | 0.013252 | 0.1016 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4663.043 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 293.043 | 0.72362 | 0.0042504 | 0.013416 | 0.10285 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4679.643 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 309.643 | 0.76461 | 0.0044912 | 0.013452 | 0.10313 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4683.543 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 313.543 | 0.76974 | 0.004495 | 0.013304 | 0.102 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4698.043 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 328.043 | 0.80534 | 0.0047029 | 0.013335 | 0.10224 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4701.943 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 331.943 | 0.81968 | 0.0048146 | 0.0135 | 0.1035 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4718.543 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 348.543 | 0.86067 | 0.0050554 | 0.013536 | 0.10378 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4722.443 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 352.443 | 0.86524 | 0.0050527 | 0.013388 | 0.10264 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4736.943 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 366.943 | 0.90084 | 0.0052605 | 0.013419 | 0.10288 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4740.843 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 370.843 | 0.91574 | 0.0053788 | 0.013585 | 0.10415 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4757.443 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 387.443 | 0.95673 | 0.0056196 | 0.013621 | 0.10443 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4761.343 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 391.343 | 0.96074 | 0.0056103 | 0.013472 | 0.10328 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4775.843 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 405.843 | 0.99634 | 0.0058182 | 0.013503 | 0.10352 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4779.743 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 409.743 | 1.0118 | 0.005943 | 0.01367 | 0.1048 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4796.343 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 426.343 | 1.0528 | 0.0061838 | 0.013706 | 0.10508 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4800.243 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 430.243 | 1.0562 | 0.006168 | 0.013555 | 0.10392 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4814.743 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 444.743 | 1.0918 | 0.0063759 | 0.013586 | 0.10416 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4818.643 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 448.643 | 1.1079 | 0.0065073 | 0.013754 | 0.10545 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4835.243 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 465.243 | 1.1488 | 0.006748 | 0.01379 | 0.10573 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4839.143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 469.143 | 1.1517 | 0.0067257 | 0.013639 | 0.10456 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4853.643 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 483.643 | 1.1873 | 0.0069336 | 0.01367 | 0.1048 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4857.543 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 487.543 | 1.2039 | 0.0070715 | 0.013839 | 0.1061 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4874.143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 504.143 | 1.2449 | 0.0073122 | 0.013875 | 0.10638 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4878.043 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 508.043 | 1.2472 | 0.0072834 | 0.013723 | 0.10521 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4892.543 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 522.543 | 1.2828 | 0.0074912 | 0.013754 | 0.10544 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4896.443 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 526.443 | 1.3 | 0.0076357 | 0.013924 | 0.10675 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4913.043 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 543.043 | 1.341 | 0.0078765 | 0.01396 | 0.10702 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4916.943 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 546.943 | 1.3427 | 0.007841 | 0.013806 | 0.10585 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4931.443 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 561.443 | 1.3783 | 0.0080489 | 0.013837 | 0.10609 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4935.343 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 565.343 | 1.396 | 0.0081999 | 0.014008 | 0.1074 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4951.943 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 581.943 | 1.437 | 0.0084407 | 0.014044 | 0.10767 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4955.843 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 585.843 | 1.4382 | 0.0083987 | 0.01389 | 0.10649 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4970.343 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 600.343 | 1.4738 | 0.0086066 | 0.013921 | 0.10673 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4974.243 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 604.243 | 1.4921 | 0.0087641 | 0.014093 | 0.10804 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 4990.843 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 620.843 | 1.5331 | 0.0090049 | 0.014129 | 0.10832 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 4994.743 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 624.743 | 1.5337 | 0.0089564 | 0.013973 | 0.10713 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5009.243 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 639.243 | 1.5693 | 0.0091643 | 0.014005 | 0.10737 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5013.143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 643.143 | 1.5881 | 0.0093283 | 0.014177 | 0.10869 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5029.743 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 656.257 | 1.6205 | 0.0095186 | 0.014206 | 0.10891 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5033.643 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 652.357 | 1.6015 | 0.0093523 | 0.014033 | 0.10759 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5048.143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 637.857 | 1.5659 | 0.0091444 | 0.014002 | 0.10735 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5052.043 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 633.957 | 1.5655 | 0.0091951 | 0.014157 | 0.10854 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5068.643 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 617.357 | 1.5245 | 0.0089543 | 0.014121 | 0.10826 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5072.543 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 613.457 | 1.506 | 0.0087946 | 0.013949 | 0.10694 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5087.043 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 598.957 | 1.4704 | 0.0085867 | 0.013918 | 0.1067 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5090.943 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 595.057 | 1.4694 | 0.0086309 | 0.014073 | 0.10789 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5107.543 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 578.457 | 1.4284 | 0.0083901 | 0.014037 | 0.10761 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5111.443 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 574.557 | 1.4105 | 0.0082369 | 0.013866 | 0.1063 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5125.943 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 560.057 | 1.3749 | 0.008029 | 0.013834 | 0.10606 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5129.843 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 556.157 | 1.3733 | 0.0080667 | 0.013988 | 0.10724 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5146.443 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 539.557 | 1.3323 | 0.0078259 | 0.013952 | 0.10697 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5150.343 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 535.657 | 1.315 | 0.0076792 | 0.013782 | 0.10566 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5164.843 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 521.157 | 1.2794 | 0.0074714 | 0.013751 | 0.10542 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5168.743 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 517.257 | 1.2773 | 0.0075025 | 0.013904 | 0.10659 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5185.343 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 500.657 | 1.2363 | 0.0072617 | 0.013867 | 0.10632 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5189.243 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 496.757 | 1.2195 | 0.0071216 | 0.013698 | 0.10502 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5203.743 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 482.257 | 1.1839 | 0.0069137 | 0.013667 | 0.10478 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5207.643 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 478.357 | 1.1812 | 0.0069382 | 0.013819 | 0.10595 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5224.243 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 461.757 | 1.1402 | 0.0066975 | 0.013783 | 0.10567 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5228.143 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 457.857 | 1.124 | 0.0065639 | 0.013615 | 0.10438 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5242.643 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 443.357 | 1.0884 | 0.006356 | 0.013583 | 0.10414 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5246.543 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 439.457 | 1.0852 | 0.006374 | 0.013734 | 0.1053 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5263.143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 422.857 | 1.0442 | 0.0061332 | 0.013698 | 0.10502 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5267.043 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 418.957 | 1.0285 | 0.0060062 | 0.013531 | 0.10374 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5281.543 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 404.457 | 0.99293 | 0.0057983 | 0.0135 | 0.1035 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5285.443 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 400.557 | 0.98911 | 0.0058098 | 0.01365 | 0.10465 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5302.043 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 383.957 | 0.94812 | 0.005569 | 0.013614 | 0.10437 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5305.943 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 380.057 | 0.93303 | 0.0054485 | 0.013447 | 0.1031 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5320.443 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 365.557 | 0.89743 | 0.0052407 | 0.013416 | 0.10286 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5324.343 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 361.657 | 0.89305 | 0.0052456 | 0.013565 | 0.104 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5340.943 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 345.057 | 0.85206 | 0.0050048 | 0.013529 | 0.10372 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5344.843 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 341.157 | 0.83753 | 0.0048909 | 0.013364 | 0.10245 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5359.343 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 326.657 | 0.80194 | 0.004683 | 0.013332 | 0.10222 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5363.243 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 322.757 | 0.797 | 0.0046814 | 0.01348 | 0.10335 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5379.843 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 306.157 | 0.756 | 0.0044406 | 0.013444 | 0.10307 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5383.743 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 302.257 | 0.74203 | 0.0043332 | 0.01328 | 0.10181 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5398.243 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 287.757 | 0.70644 | 0.0041253 | 0.013249 | 0.10157 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5402.143 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 283.857 | 0.70094 | 0.0041171 | 0.013396 | 0.1027 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA1 | LO | 5418.743 | 0.3 | -0.079158 | 5.4009 | 13.3356 | 0.072024 | 267.257 | 0.60682 | 0.0032774 | 0.011295 | 0.086597 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA1 | LO | 5422.643 | 0.3 | 0.099551 | 6.7923 | 16.7711 | 0.11391 | 263.357 | 0.75201 | 0.0051079 | 0.017853 | 0.13688 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMT1 | HI | 5433.953 | 0.3 | 0.16088 | 75.773 | 8.0963 | 0.61348 | 252.047 | 8.029 | 0.60838 | 0.18328 | 1.4051 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMT1 | HI | 5436.903 | 0.3 | -0.18947 | 89.2401 | 9.5352 | 0.85093 | 249.097 | 9.3453 | 0.83397 | 0.25273 | 1.9376 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA2 | HI | 5450.403 | 0.3 | 0.16713 | 78.7149 | 8.4106 | 0.66204 | 235.597 | 7.7963 | 0.61369 | 0.19136 | 1.4671 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA2 | HI | 5460.933 | 0.3 | -0.1468 | 69.1418 | 7.3878 | 0.5108 | 225.067 | 6.5421 | 0.45233 | 0.14447 | 1.1076 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA3 | HI | 5472.485 | 0.3 | 0.10723 | 50.5027 | 5.3962 | 0.27252 | 213.515 | 4.5332 | 0.22894 | 0.075219 | 0.57668 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA3 | HI | 5483.585 | 0.3 | -0.12488 | 58.8168 | 6.2845 | 0.36964 | 202.415 | 5.005 | 0.29438 | 0.099602 | 0.76362 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMT2 | HI | 5490.985 | 0.3 | 0.13944 | 65.6748 | 7.0173 | 0.46086 | 195.015 | 5.3843 | 0.35361 | 0.12217 | 0.93665 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMT2 | HI | 5499.285 | 0.3 | -0.13006 | 61.2584 | 6.5454 | 0.40096 | 186.715 | 4.8085 | 0.29456 | 0.10433 | 0.79985 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 5508.485 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 177.515 | 6.923 | 0.64222 | 0.23426 | 1.796 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDRF | HI | 5512.245 | 0.3 | -0.19873 | 93.5985 | 10.0009 | 0.93607 | 173.755 | 6.8371 | 0.63994 | 0.2364 | 1.8124 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFRF | HI | 5516.005 | 0.3 | 0.21047 | 99.1305 | 10.592 | 1.05 | 169.995 | 7.0845 | 0.70229 | 0.26284 | 2.0151 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDRF | HI | 5519.765 | 0.3 | -0.19873 | 93.5985 | 10.0009 | 0.93607 | 166.235 | 6.5412 | 0.61224 | 0.23225 | 1.7806 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 5523.525 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 162.475 | 6.3364 | 0.58781 | 0.2261 | 1.7334 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 5527.275 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 158.725 | 5.6165 | 0.47274 | 0.18446 | 1.4142 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 5531.025 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 154.975 | 6.0439 | 0.56068 | 0.22203 | 1.7022 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 5534.775 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 151.225 | 5.3511 | 0.4504 | 0.18111 | 1.3885 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 5538.525 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 147.475 | 5.7514 | 0.53354 | 0.21796 | 1.671 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 5542.275 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 143.725 | 5.0857 | 0.42807 | 0.17776 | 1.3628 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 5546.025 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 139.975 | 5.4589 | 0.50641 | 0.21389 | 1.6398 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 5549.775 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 136.225 | 4.8203 | 0.40573 | 0.17441 | 1.3371 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 5553.525 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 132.475 | 5.1664 | 0.47927 | 0.20982 | 1.6086 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 5557.275 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 128.725 | 4.555 | 0.38339 | 0.17106 | 1.3114 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 5561.025 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 124.975 | 4.8739 | 0.45214 | 0.20575 | 1.5774 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 5564.775 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 121.225 | 4.2896 | 0.36105 | 0.16771 | 1.2857 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 5568.525 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 117.475 | 4.5814 | 0.42501 | 0.20168 | 1.5462 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 5572.275 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 113.725 | 4.0242 | 0.33872 | 0.16435 | 1.2601 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 5576.025 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 109.975 | 4.289 | 0.39787 | 0.19761 | 1.515 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 5579.775 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 106.225 | 3.7588 | 0.31638 | 0.161 | 1.2344 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 5583.525 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 102.475 | 3.9965 | 0.37074 | 0.19354 | 1.4838 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 5587.275 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 98.725 | 3.4934 | 0.29404 | 0.15765 | 1.2087 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 5591.025 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 94.975 | 3.704 | 0.34361 | 0.18947 | 1.4526 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDWH | HI | 5594.775 | 0.3 | -0.17871 | 84.17 | 8.9935 | 0.75698 | 91.225 | 3.228 | 0.2717 | 0.1543 | 1.183 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFWH | HI | 5598.525 | 0.3 | 0.19696 | 92.7669 | 9.9121 | 0.91951 | 87.475 | 3.4115 | 0.31647 | 0.1854 | 1.4214 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMT2 | HI | 5607.725 | 0.3 | -0.13006 | 61.2584 | 6.5454 | 0.40096 | 78.275 | 2.0158 | 0.12349 | 0.078667 | 0.60312 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMT2 | HI | 5616.025 | 0.3 | 0.13944 | 65.6748 | 7.0173 | 0.46086 | 69.975 | 1.932 | 0.12688 | 0.088162 | 0.67591 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA3 | HI | 5623.425 | 0.3 | -0.12488 | 58.8168 | 6.2845 | 0.36964 | 62.575 | 1.5473 | 0.091005 | 0.069096 | 0.52974 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA3 | HI | 5634.525 | 0.3 | 0.10723 | 50.5027 | 5.3962 | 0.27252 | 51.475 | 1.0929 | 0.055194 | 0.049157 | 0.37687 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA2 | HI | 5646.077 | 0.3 | -0.1468 | 69.1418 | 7.3878 | 0.5108 | 39.923 | 1.1605 | 0.080236 | 0.088656 | 0.67969 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA2 | HI | 5656.607 | 0.3 | 0.16713 | 78.7149 | 8.4106 | 0.66204 | 29.393 | 0.97267 | 0.076563 | 0.11079 | 0.8494 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMT1 | HI | 5670.107 | 0.3 | -0.18947 | 89.2401 | 9.5352 | 0.85093 | 15.893 | 0.59625 | 0.053209 | 0.13562 | 1.0398 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMT1 | HI | 5673.057 | 0.3 | 0.16088 | 75.773 | 8.0963 | 0.61348 | 12.943 | 0.4123 | 0.031241 | 0.096708 | 0.74143 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA1 | LO | 5684.367 | 0.3 | 0.099551 | 6.7923 | 16.7711 | 0.11391 | 1.633 | 0.0046629 | 3.1672e-05 | 0.017092 | 0.13104 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA1 | LO | 5688.267 | 0.3 | -0.079158 | 5.4009 | 13.3356 | 0.072024 | 2.267 | 0.0051474 | 2.7801e-05 | 0.010808 | 0.08286 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5704.867 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 18.867 | 0.046589 | 0.00027365 | 0.012819 | 0.098281 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5708.767 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 22.767 | 0.055893 | 0.00032639 | 0.012679 | 0.097205 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5723.267 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 37.267 | 0.09149 | 0.00053426 | 0.01271 | 0.097444 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5727.167 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 41.167 | 0.10166 | 0.0005971 | 0.012868 | 0.098653 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5743.767 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 57.767 | 0.14265 | 0.00083787 | 0.012904 | 0.09893 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5747.667 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 61.667 | 0.15139 | 0.00088406 | 0.012763 | 0.097847 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5762.167 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 76.167 | 0.18699 | 0.0010919 | 0.012794 | 0.098086 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5766.067 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 80.067 | 0.19771 | 0.0011613 | 0.012952 | 0.099302 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5782.667 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 96.667 | 0.2387 | 0.0014021 | 0.012989 | 0.099579 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5786.567 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 100.567 | 0.24689 | 0.0014417 | 0.012846 | 0.098488 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5801.067 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 115.067 | 0.28249 | 0.0016496 | 0.012877 | 0.098727 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5804.967 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 118.967 | 0.29377 | 0.0017255 | 0.013037 | 0.09995 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5821.567 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 135.567 | 0.33476 | 0.0019663 | 0.013073 | 0.10023 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5825.467 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 139.467 | 0.34239 | 0.0019994 | 0.01293 | 0.099129 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5839.967 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 153.967 | 0.37799 | 0.0022073 | 0.012961 | 0.099368 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5843.867 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 157.867 | 0.38983 | 0.0022898 | 0.013122 | 0.1006 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5860.467 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 174.467 | 0.43082 | 0.0025305 | 0.013158 | 0.10088 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5864.367 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 178.367 | 0.43789 | 0.0025571 | 0.013014 | 0.099771 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5878.867 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 192.867 | 0.47348 | 0.002765 | 0.013045 | 0.10001 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5882.767 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 196.767 | 0.48588 | 0.002854 | 0.013206 | 0.10125 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5899.367 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 213.367 | 0.52688 | 0.0030947 | 0.013242 | 0.10153 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5903.267 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 217.267 | 0.53339 | 0.0031148 | 0.013097 | 0.10041 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5917.767 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 231.767 | 0.56898 | 0.0033226 | 0.013128 | 0.10065 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5921.667 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 235.667 | 0.58194 | 0.0034182 | 0.013291 | 0.1019 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5938.267 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 252.267 | 0.62293 | 0.003659 | 0.013327 | 0.10217 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5942.167 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 256.167 | 0.62888 | 0.0036724 | 0.013181 | 0.10105 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5956.667 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 270.667 | 0.66448 | 0.0038803 | 0.013212 | 0.10129 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5960.567 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 274.567 | 0.678 | 0.0039824 | 0.013376 | 0.10255 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5977.167 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 291.167 | 0.71899 | 0.0042232 | 0.013412 | 0.10282 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5981.067 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 295.067 | 0.72438 | 0.0042301 | 0.013265 | 0.10169 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 5995.567 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 309.567 | 0.75998 | 0.004438 | 0.013296 | 0.10193 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 5999.467 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 313.467 | 0.77406 | 0.0045466 | 0.01346 | 0.10319 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6016.067 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 330.067 | 0.81505 | 0.0047874 | 0.013496 | 0.10347 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6019.967 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 333.967 | 0.81988 | 0.0047878 | 0.013348 | 0.10234 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6034.467 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 348.467 | 0.85548 | 0.0049957 | 0.013379 | 0.10257 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6038.367 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 352.367 | 0.87011 | 0.0051108 | 0.013545 | 0.10384 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6054.967 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 368.967 | 0.9111 | 0.0053516 | 0.013581 | 0.10412 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6058.867 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 372.867 | 0.91538 | 0.0053455 | 0.013432 | 0.10298 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6073.367 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 387.367 | 0.95098 | 0.0055533 | 0.013463 | 0.10322 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6077.267 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 391.267 | 0.96617 | 0.0056751 | 0.013629 | 0.10449 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6093.867 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 407.867 | 1.0072 | 0.0059158 | 0.013666 | 0.10477 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6097.767 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 411.767 | 1.0109 | 0.0059031 | 0.013515 | 0.10362 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6112.267 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 426.267 | 1.0465 | 0.006111 | 0.013547 | 0.10386 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6116.167 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 430.167 | 1.0622 | 0.0062393 | 0.013714 | 0.10514 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6132.767 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 446.767 | 1.1032 | 0.00648 | 0.01375 | 0.10542 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6136.667 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 450.667 | 1.1064 | 0.0064608 | 0.013599 | 0.10426 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6151.167 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 465.167 | 1.142 | 0.0066687 | 0.01363 | 0.1045 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6155.067 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 469.067 | 1.1583 | 0.0068035 | 0.013799 | 0.10579 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6171.667 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 485.667 | 1.1993 | 0.0070443 | 0.013835 | 0.10607 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6175.567 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 489.567 | 1.2019 | 0.0070185 | 0.013683 | 0.1049 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6190.067 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 504.067 | 1.2375 | 0.0072264 | 0.013714 | 0.10514 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6193.967 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 507.967 | 1.2543 | 0.0073677 | 0.013883 | 0.10644 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6210.567 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 524.567 | 1.2953 | 0.0076085 | 0.013919 | 0.10672 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6214.467 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 528.467 | 1.2974 | 0.0075762 | 0.013766 | 0.10554 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6228.967 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 542.967 | 1.333 | 0.007784 | 0.013798 | 0.10578 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6232.867 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 546.867 | 1.3504 | 0.0079319 | 0.013968 | 0.10709 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6249.467 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 563.467 | 1.3914 | 0.0081727 | 0.014004 | 0.10736 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6253.367 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 567.367 | 1.3929 | 0.0081338 | 0.01385 | 0.10618 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6267.867 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 581.867 | 1.4285 | 0.0083417 | 0.013881 | 0.10642 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6271.767 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 585.767 | 1.4465 | 0.0084961 | 0.014053 | 0.10774 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6288.367 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 602.367 | 1.4874 | 0.0087369 | 0.014089 | 0.10801 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6292.267 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 606.267 | 1.4884 | 0.0086915 | 0.013934 | 0.10683 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6306.767 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 620.767 | 1.524 | 0.0088994 | 0.013965 | 0.10706 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6310.667 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 624.667 | 1.5425 | 0.0090604 | 0.014137 | 0.10839 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6327.267 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 641.267 | 1.5835 | 0.0093011 | 0.014173 | 0.10866 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6331.167 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 645.167 | 1.5839 | 0.0092492 | 0.014017 | 0.10747 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6345.667 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 659.667 | 1.6195 | 0.0094571 | 0.014049 | 0.10771 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6349.567 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 663.567 | 1.6386 | 0.0096246 | 0.014222 | 0.10903 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6366.167 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 680.167 | 1.6796 | 0.0098654 | 0.014258 | 0.10931 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6370.067 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 684.067 | 1.6794 | 0.0098069 | 0.014101 | 0.10811 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6384.567 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 698.567 | 1.715 | 0.010015 | 0.014132 | 0.10835 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6388.467 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 702.467 | 1.7346 | 0.010189 | 0.014307 | 0.10968 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6405.067 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 719.067 | 1.7756 | 0.01043 | 0.014343 | 0.10996 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6408.967 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 722.967 | 1.7749 | 0.010365 | 0.014185 | 0.10875 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6423.467 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 737.467 | 1.8105 | 0.010572 | 0.014216 | 0.10899 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6427.367 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 741.367 | 1.8307 | 0.010753 | 0.014391 | 0.11033 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6443.967 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 757.967 | 1.8717 | 0.010994 | 0.014427 | 0.11061 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6447.867 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 761.867 | 1.8704 | 0.010922 | 0.014268 | 0.10939 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFA | LO | 6462.367 | 0.3 | 0.085588 | 5.8396 | 14.4188 | 0.0842 | 776.367 | 1.906 | 0.01113 | 0.0143 | 0.10963 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDA | LO | 6466.267 | 0.3 | -0.086089 | 5.8738 | 14.5031 | 0.085188 | 780.267 | 1.9267 | 0.011317 | 0.014476 | 0.11098 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMA1 | LO | 6482.867 | 0.3 | -0.079158 | 5.4009 | 13.3356 | 0.072024 | 796.867 | 1.8093 | 0.009772 | 0.012269 | 0.094066 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMA1 | LO | 6486.767 | 0.3 | 0.099551 | 6.7923 | 16.7711 | 0.11391 | 800.767 | 2.2866 | 0.015531 | 0.019417 | 0.14886 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMS1 | HI | 6497.577 | 0.3 | 0.10471 | 49.3192 | 5.2697 | 0.2599 | 811.577 | 16.8271 | 0.8299 | 0.16347 | 1.2533 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMS1 | HI | 6498.877 | 0.3 | -0.13416 | 63.1859 | 6.7514 | 0.42659 | 812.877 | 21.5928 | 1.3644 | 0.26864 | 2.0596 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFMS2 | LO | 6514.91 | 0.3 | 0.070722 | 4.8253 | 11.9143 | 0.05749 | 828.91 | 1.6815 | 0.0081138 | 0.0098406 | 0.075445 | 1 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDMS2 | LO | 6521.115 | 0.3 | -0.087962 | 6.0016 | 14.8187 | 0.088936 | 835.115 | 2.1071 | 0.012646 | 0.015237 | 0.11682 | 1 | 0 | 0 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFI | LO | 6532.4874 | 0.3 | 0.076749 | 5.2365 | 12.9296 | 0.067706 | 846.4874 | 1.8635 | 0.0097582 | 0.01162 | 0.089084 | 1 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDI | LO | 6546.0474 | 0.3 | -0.070481 | 4.8089 | 11.8738 | 0.0571 | 860.0474 | 1.7387 | 0.0083613 | 0.0098191 | 0.07528 | 1 | 0 | 0 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFI | LO | 6559.6074 | 0.3 | 0.076749 | 5.2365 | 12.9296 | 0.067706 | 873.6074 | 1.9232 | 0.010071 | 0.011667 | 0.089444 | 1 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDI | LO | 6573.1674 | 0.3 | -0.070481 | 4.8089 | 11.8738 | 0.0571 | 887.1674 | 1.7936 | 0.008625 | 0.0098587 | 0.075583 | 1 | 0 | 0 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFI | LO | 6586.7274 | 0.3 | 0.076749 | 5.2365 | 12.9296 | 0.067706 | 900.7274 | 1.9829 | 0.010383 | 0.011713 | 0.089803 | 1 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDI | LO | 6600.2874 | 0.3 | -0.070481 | 4.8089 | 11.8738 | 0.0571 | 914.2874 | 1.8484 | 0.0088886 | 0.0098982 | 0.075886 | 1 | 0 | 0 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFI | LO | 6613.8474 | 0.3 | 0.076749 | 5.2365 | 12.9296 | 0.067706 | 927.8474 | 2.0426 | 0.010696 | 0.01176 | 0.090163 | 1 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDI | LO | 6627.4074 | 0.3 | -0.070481 | 4.8089 | 11.8738 | 0.0571 | 941.4074 | 1.9032 | 0.0091523 | 0.0099378 | 0.07619 | 1 | 0 | 0 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFI | LO | 6640.9674 | 0.3 | 0.076749 | 5.2365 | 12.9296 | 0.067706 | 954.9674 | 2.1023 | 0.011009 | 0.011807 | 0.090522 | 1 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDI | LO | 6654.5274 | 0.3 | -0.070481 | 4.8089 | 11.8738 | 0.0571 | 968.5274 | 1.958 | 0.0094159 | 0.0099773 | 0.076493 | 1 | 0 | 0 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFI | LO | 6668.0874 | 0.3 | 0.076749 | 5.2365 | 12.9296 | 0.067706 | 982.0874 | 2.162 | 0.011321 | 0.011854 | 0.090882 | 1 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDI | LO | 6681.6474 | 0.3 | -0.070481 | 4.8089 | 11.8738 | 0.0571 | 995.6474 | 2.0129 | 0.0096796 | 0.010017 | 0.076796 | 1 | 0 | 0 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QFI | LO | 6695.0574 | 0.15 | 0.038374 | 2.6183 | 6.4648 | 0.016927 | 1009.0574 | 1.1107 | 0.0029081 | 0.0029752 | 0.02281 | 1 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum |  |  |  | 0.28175 | [12 empty] | QFI | QDI | QDMS2 | QFMS2 | QDMS1 | QFMS1 | QFMA1 | QDMA1 | QDA | QFA | QFMT1 | QDMT1 | QFMA2 | QDMA2 | QFMA3 | QDMA3 | QFMT2 | QDMT2 | QFWH | QDRF | QFRF | QDWH | QFMINJ1 | QDMINJ1 | QFMINJ2 | QDMINJ2 | QFMINJ3 | QDMINJ3 | QFINJ4H | QDINJ2 | QFINJ3 | QFINJ1 | QDINJ1 | QFINJ2H | Total Magnets
Total | [6 empty] | 190.4906 | 307196.0952 |  | 160.1775 | 52.6002 | 403.2684 | 599 | 137 | 12 | Number of Magnets | 14 | 12 | 2 | 2 | 2 | 2 | 12 | 12 | 240 | 240 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 48 | 8 | 4 | 40 | 2 | 2 | 2 | 2 | 6 | 6 | 2 | 2 | 2 | 8 | 8 | 4 | 748
Average | [7 empty] | 410.69 | [7 empty] | Avg 1-way cable distance (m) | 932.158 | 932.1687 | 839.4363 | 833.2313 | 817.1983 | 815.8983 | 356.6215 | 357.6493 | 425.2493 | 425.2493 | 125.9807 | 125.938 | 125.938 | 125.938 | 125.938 | 125.938 | 125.938 | 125.938 | 125.938 | 125.938 | 125.938 | 125.938 | 820.3697 | 821.6697 | 837.6547 | 843.8387 | 885.26 | 900.06 | 944.46 | 959.11 | 965.762 | 995.1782 | 995.346 | 995.346
[6 empty] | LO | 45.922 |  |  | 3.5424
[6 empty] | HI | 144.5687 |  |  | 156.6351

## Quadrupole Family Cables
Quadrupole Family | Count | Avg 1-way cable distance
QFI | 13 | 932.158
QDI | 12 | 932.1687
QDMS2 | 2 | 839.4363
QFMS2 | 2 | 833.2313
QDMS1 | 2 | 817.1983
QFMS1 | 2 | 815.8983
QFMA1 | 12 | 356.6215
QDMA1 | 12 | 357.6493
QDA | 240 | 425.2493
QFA | 240 | 425.2493
QFMT1 | 8 | 125.9807
QDMT1 | 8 | 125.938
QFMA2 | 8 | 125.938
QDMA2 | 8 | 125.938
QFMA3 | 8 | 125.938
QDMA3 | 8 | 125.938
QFMT2 | 8 | 125.938
QDMT2 | 8 | 125.938
QFWH | 48 | 125.938
QDRF | 8 | 125.938
QFRF | 4 | 125.938
QDWH | 40 | 125.938
QFMINJ1 | 2 | 820.3697
QDMINJ1 | 2 | 821.6697
QFMINJ2 | 2 | 837.6547
QDMINJ2 | 2 | 843.8387
QFMINJ3 | 6 | 885.26
QDMINJ3 | 6 | 900.06
QFINJ4H | 2 | 944.46
QDINJ2 | 2 | 959.11
QFINJ3 | 2 | 965.762
QFINJ1 | 8 | 995.1782
QDINJ1 | 8 | 995.346
QFINJ2H | 4 | 995.346
Total | 747 | 409.9919

## Sextupoles
Name | s [m] | Length [m] | k2L [m^-3] | Current [A] | Voltage [V] | Power [kW] | Nearest Alcove [m] | Total Cable Voltage [V] | Total Cable Power [kW] | Power Supply Loss [kW] | Total Power [kW] |  | SD | SF | SD1 | SF1
SF1 | 208.0903 | 0.25 | 0 | 0 | 0 | 0 | 809.9097 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1
SD1 | 212.9403 | 0.25 | 0 | 0 | 0 | 0 | 805.0597 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1 | 0
SD | 228.5903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 789.4097 | 6.0501 | 0.034596 | 0.0055505 | 0.042554 |  | 1 | 0 | 0 | 0
SF | 233.4403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 784.5597 | 3.8959 | 0.014434 | 0.0023167 | 0.017761 |  | 0 | 1 | 0 | 0
SF | 246.9903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 771.0097 | 3.8286 | 0.014185 | 0.0022793 | 0.017475 |  | 0 | 1 | 0 | 0
SD | 251.8403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 766.1597 | 5.8719 | 0.033577 | 0.0053976 | 0.041382 |  | 1 | 0 | 0 | 0
SD | 267.4903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 750.5097 | 5.752 | 0.032891 | 0.0052948 | 0.040593 |  | 1 | 0 | 0 | 0
SF | 272.3403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 745.6597 | 3.7027 | 0.013718 | 0.0022093 | 0.016938 |  | 0 | 1 | 0 | 0
SF | 285.8903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 732.1097 | 3.6354 | 0.013469 | 0.0021719 | 0.016652 |  | 0 | 1 | 0 | 0
SD | 290.7403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 727.2597 | 5.5738 | 0.031872 | 0.0051419 | 0.039421 |  | 1 | 0 | 0 | 0
SD | 306.3903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 711.6097 | 5.4539 | 0.031187 | 0.005039 | 0.038633 |  | 1 | 0 | 0 | 0
SF | 311.2403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 706.7597 | 3.5096 | 0.013003 | 0.002102 | 0.016115 |  | 0 | 1 | 0 | 0
SF | 324.7903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 693.2097 | 3.4423 | 0.012753 | 0.0020646 | 0.015828 |  | 0 | 1 | 0 | 0
SD | 329.6403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 688.3597 | 5.2757 | 0.030168 | 0.0048862 | 0.037461 |  | 1 | 0 | 0 | 0
SD | 345.2903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 672.7097 | 5.1557 | 0.029482 | 0.0047833 | 0.036672 |  | 1 | 0 | 0 | 0
SF | 350.1403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 667.8597 | 3.3164 | 0.012287 | 0.0019946 | 0.015292 |  | 0 | 1 | 0 | 0
SF | 363.6903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 654.3097 | 3.2491 | 0.012038 | 0.0019572 | 0.015005 |  | 0 | 1 | 0 | 0
SD | 368.5403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 649.4597 | 4.9775 | 0.028463 | 0.0046305 | 0.0355 |  | 1 | 0 | 0 | 0
SD | 384.1903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 633.8097 | 4.8576 | 0.027777 | 0.0045276 | 0.034711 |  | 1 | 0 | 0 | 0
SF | 389.0403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 628.9597 | 3.1232 | 0.011571 | 0.0018873 | 0.014469 |  | 0 | 1 | 0 | 0
SF | 402.5903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 615.4097 | 3.0559 | 0.011322 | 0.0018499 | 0.014182 |  | 0 | 1 | 0 | 0
SD | 407.4403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 610.5597 | 4.6794 | 0.026758 | 0.0043747 | 0.03354 |  | 1 | 0 | 0 | 0
SD | 423.0903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 594.9097 | 4.5595 | 0.026072 | 0.0042719 | 0.032751 |  | 1 | 0 | 0 | 0
SF | 427.9403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 590.0597 | 2.9301 | 0.010856 | 0.0017799 | 0.013646 |  | 0 | 1 | 0 | 0
SF | 441.4903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 576.5097 | 2.8628 | 0.010606 | 0.0017425 | 0.013359 |  | 0 | 1 | 0 | 0
SD | 446.3403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 571.6597 | 4.3813 | 0.025053 | 0.004119 | 0.031579 |  | 1 | 0 | 0 | 0
SD | 461.9903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 556.0097 | 4.2613 | 0.024367 | 0.0040161 | 0.03079 |  | 1 | 0 | 0 | 0
SF | 466.8403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 551.1597 | 2.7369 | 0.01014 | 0.0016726 | 0.012823 |  | 0 | 1 | 0 | 0
SF | 480.3903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 537.6097 | 2.6696 | 0.0098908 | 0.0016352 | 0.012536 |  | 0 | 1 | 0 | 0
SD | 485.2403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 532.7597 | 4.0831 | 0.023348 | 0.0038633 | 0.029619 |  | 1 | 0 | 0 | 0
SD | 500.8903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 517.1097 | 3.9632 | 0.022663 | 0.0037604 | 0.02883 |  | 1 | 0 | 0 | 0
SF | 505.7403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 512.2597 | 2.5437 | 0.0094244 | 0.0015652 | 0.012 |  | 0 | 1 | 0 | 0
SF | 519.2903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 498.7097 | 2.4764 | 0.0091751 | 0.0015278 | 0.011713 |  | 0 | 1 | 0 | 0
SD | 524.1403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 493.8597 | 3.785 | 0.021644 | 0.0036076 | 0.027658 |  | 1 | 0 | 0 | 0
SD | 539.7903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 478.2097 | 3.6651 | 0.020958 | 0.0035047 | 0.026869 |  | 1 | 0 | 0 | 0
SF | 544.6403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 473.3597 | 2.3506 | 0.0087087 | 0.0014579 | 0.011177 |  | 0 | 1 | 0 | 0
SF | 558.1903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 459.8097 | 2.2833 | 0.0084594 | 0.0014205 | 0.01089 |  | 0 | 1 | 0 | 0
SD | 563.0403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 454.9597 | 3.4869 | 0.019939 | 0.0033519 | 0.025698 |  | 1 | 0 | 0 | 0
SD | 578.6903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 439.3097 | 3.3669 | 0.019253 | 0.003249 | 0.024909 |  | 1 | 0 | 0 | 0
SF | 583.5403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 434.4597 | 2.1574 | 0.0079931 | 0.0013505 | 0.010354 |  | 0 | 1 | 0 | 0
SF | 597.0903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 420.9097 | 2.0901 | 0.0077438 | 0.0013131 | 0.010067 |  | 0 | 1 | 0 | 0
SD | 601.9403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 416.0597 | 3.1887 | 0.018234 | 0.0030961 | 0.023737 |  | 1 | 0 | 0 | 0
SD | 617.5903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 400.4097 | 3.0688 | 0.017548 | 0.0029933 | 0.022948 |  | 1 | 0 | 0 | 0
SF | 622.4403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 395.5597 | 1.9642 | 0.0072774 | 0.0012432 | 0.009531 |  | 0 | 1 | 0 | 0
SF | 635.9903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 382.0097 | 1.897 | 0.0070281 | 0.0012058 | 0.0092443 |  | 0 | 1 | 0 | 0
SD | 640.8403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 377.1597 | 2.8906 | 0.016529 | 0.0028404 | 0.021777 |  | 1 | 0 | 0 | 0
SD | 656.4903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 361.5097 | 2.7707 | 0.015843 | 0.0027375 | 0.020988 |  | 1 | 0 | 0 | 0
SF | 661.3403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 356.6597 | 1.7711 | 0.0065617 | 0.0011358 | 0.008708 |  | 0 | 1 | 0 | 0
SF | 674.8903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 343.1097 | 1.7038 | 0.0063124 | 0.0010984 | 0.0084213 |  | 0 | 1 | 0 | 0
SD | 679.7403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 338.2597 | 2.5925 | 0.014824 | 0.0025847 | 0.019816 |  | 1 | 0 | 0 | 0
SD | 695.3903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 322.6097 | 2.4725 | 0.014138 | 0.0024818 | 0.019027 |  | 1 | 0 | 0 | 0
SF | 700.2403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 317.7597 | 1.5779 | 0.0058461 | 0.0010285 | 0.007885 |  | 0 | 1 | 0 | 0
SF | 713.7903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 304.2097 | 1.5106 | 0.0055968 | 0.00099108 | 0.0075983 |  | 0 | 1 | 0 | 0
SD | 718.6403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 299.3597 | 2.2943 | 0.01312 | 0.002329 | 0.017855 |  | 1 | 0 | 0 | 0
SD | 734.2903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 283.7097 | 2.1744 | 0.012434 | 0.0022261 | 0.017067 |  | 1 | 0 | 0 | 0
SF | 739.1403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 278.8597 | 1.3847 | 0.0051304 | 0.00092112 | 0.0070619 |  | 0 | 1 | 0 | 0
SF | 752.6903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 265.3097 | 1.3175 | 0.0048811 | 0.00088373 | 0.0067753 |  | 0 | 1 | 0 | 0
SD | 757.5403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 260.4597 | 1.9962 | 0.011415 | 0.0020733 | 0.015895 |  | 1 | 0 | 0 | 0
SD | 773.1903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 244.8097 | 1.8763 | 0.010729 | 0.0019704 | 0.015106 |  | 1 | 0 | 0 | 0
SF | 778.0403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 239.9597 | 1.1916 | 0.0044147 | 0.00081377 | 0.0062389 |  | 0 | 1 | 0 | 0
SF | 791.5903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 226.4097 | 1.1243 | 0.0041654 | 0.00077638 | 0.0059522 |  | 0 | 1 | 0 | 0
SD | 796.4403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 221.5597 | 1.6981 | 0.0097099 | 0.0018175 | 0.013934 |  | 1 | 0 | 0 | 0
SD | 812.0903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 205.9097 | 1.5781 | 0.0090241 | 0.0017147 | 0.013146 |  | 1 | 0 | 0 | 0
SF | 816.9403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 201.0597 | 0.9984 | 0.003699 | 0.00070642 | 0.0054159 |  | 0 | 1 | 0 | 0
SF | 830.4903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 187.5097 | 0.93112 | 0.0034497 | 0.00066903 | 0.0051292 |  | 0 | 1 | 0 | 0
SD | 835.3403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 182.6597 | 1.3999 | 0.0080051 | 0.0015618 | 0.011974 |  | 1 | 0 | 0 | 0
SD | 850.9903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 167.0097 | 1.28 | 0.0073193 | 0.0014589 | 0.011185 |  | 1 | 0 | 0 | 0
SF | 855.8403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 162.1597 | 0.80524 | 0.0029834 | 0.00059907 | 0.0045929 |  | 0 | 1 | 0 | 0
SF | 869.3903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 148.6097 | 0.73795 | 0.0027341 | 0.00056168 | 0.0043062 |  | 0 | 1 | 0 | 0
SD | 874.2403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 143.7597 | 1.1018 | 0.0063003 | 0.0013061 | 0.010013 |  | 1 | 0 | 0 | 0
SD | 889.8903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 128.1097 | 0.98185 | 0.0056145 | 0.0012032 | 0.0092246 |  | 1 | 0 | 0 | 0
SF | 894.7403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 123.2597 | 0.61207 | 0.0022677 | 0.00049172 | 0.0037699 |  | 0 | 1 | 0 | 0
SF | 908.2903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 109.7097 | 0.54479 | 0.0020184 | 0.00045433 | 0.0034832 |  | 0 | 1 | 0 | 0
SD | 913.1403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 104.8597 | 0.80366 | 0.0045955 | 0.0010504 | 0.0080529 |  | 1 | 0 | 0 | 0
SD | 928.7903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 89.2097 | 0.68371 | 0.0039096 | 0.00094749 | 0.0072641 |  | 1 | 0 | 0 | 0
SF | 933.6403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 84.3597 | 0.41891 | 0.001552 | 0.00038437 | 0.0029468 |  | 0 | 1 | 0 | 0
SF | 947.1903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 70.8097 | 0.35162 | 0.0013027 | 0.00034698 | 0.0026601 |  | 0 | 1 | 0 | 0
SD | 952.0403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 65.9597 | 0.50552 | 0.0028907 | 0.00079465 | 0.0060923 |  | 1 | 0 | 0 | 0
SD | 967.6903 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 50.3097 | 0.38558 | 0.0022048 | 0.00069177 | 0.0053036 |  | 1 | 0 | 0 | 0
SF | 972.5403 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 45.4597 | 0.22574 | 0.00083635 | 0.00027702 | 0.0021238 |  | 0 | 1 | 0 | 0
SF | 986.0903 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 31.9097 | 0.15845 | 0.00058706 | 0.00023962 | 0.0018371 |  | 0 | 1 | 0 | 0
SD | 990.9403 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 27.0597 | 0.20739 | 0.0011859 | 0.00053893 | 0.0041318 |  | 1 | 0 | 0 | 0
SD1 | 1006.5903 | 0.25 | 0 | 0 | 0 | 0 | 11.4097 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1 | 0
SF1 | 1011.4403 | 0.25 | 0 | 0 | 0 | 0 | 6.5597 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1
SF1 | 1272.2143 | 0.25 | 0 | 0 | 0 | 0 | 254.2143 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1
SD1 | 1277.0643 | 0.25 | 0 | 0 | 0 | 0 | 259.0643 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1 | 0
SD | 1292.7143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 274.7143 | 2.1054 | 0.012039 | 0.002167 | 0.016613 |  | 1 | 0 | 0 | 0
SF | 1297.5643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 279.5643 | 1.3882 | 0.0051433 | 0.00092307 | 0.0070768 |  | 0 | 1 | 0 | 0
SF | 1311.1143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 293.1143 | 1.4555 | 0.0053926 | 0.00096046 | 0.0073635 |  | 0 | 1 | 0 | 0
SD | 1315.9643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 297.9643 | 2.2836 | 0.013058 | 0.0023198 | 0.017785 |  | 1 | 0 | 0 | 0
SD | 1331.6143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 313.6143 | 2.4036 | 0.013744 | 0.0024227 | 0.018574 |  | 1 | 0 | 0 | 0
SF | 1336.4643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 318.4643 | 1.5814 | 0.005859 | 0.0010304 | 0.0078999 |  | 0 | 1 | 0 | 0
SF | 1350.0143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 332.0143 | 1.6487 | 0.0061083 | 0.0010678 | 0.0081866 |  | 0 | 1 | 0 | 0
SD | 1354.8643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 336.8643 | 2.5818 | 0.014763 | 0.0025755 | 0.019746 |  | 1 | 0 | 0 | 0
SD | 1370.5143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 352.5143 | 2.7017 | 0.015449 | 0.0026784 | 0.020534 |  | 1 | 0 | 0 | 0
SF | 1375.3643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 357.3643 | 1.7746 | 0.0065747 | 0.0011378 | 0.0087229 |  | 0 | 1 | 0 | 0
SF | 1388.9143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 370.9143 | 1.8419 | 0.006824 | 0.0011752 | 0.0090096 |  | 0 | 1 | 0 | 0
SD | 1393.7643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 375.7643 | 2.8799 | 0.016468 | 0.0028312 | 0.021706 |  | 1 | 0 | 0 | 0
SD | 1409.4143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 391.4143 | 2.9998 | 0.017154 | 0.0029341 | 0.022495 |  | 1 | 0 | 0 | 0
SF | 1414.2643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 396.2643 | 1.9677 | 0.0072904 | 0.0012451 | 0.0095459 |  | 0 | 1 | 0 | 0
SF | 1427.8143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 409.8143 | 2.035 | 0.0075396 | 0.0012825 | 0.0098326 |  | 0 | 1 | 0 | 0
SD | 1432.6643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 414.6643 | 3.178 | 0.018173 | 0.003087 | 0.023667 |  | 1 | 0 | 0 | 0
SD | 1448.3143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 430.3143 | 3.298 | 0.018859 | 0.0031898 | 0.024456 |  | 1 | 0 | 0 | 0
SF | 1453.1643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 435.1643 | 2.1609 | 0.008006 | 0.0013525 | 0.010369 |  | 0 | 1 | 0 | 0
SF | 1466.7143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 448.7143 | 2.2282 | 0.0082553 | 0.0013899 | 0.010656 |  | 0 | 1 | 0 | 0
SD | 1471.5643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 453.5643 | 3.4762 | 0.019878 | 0.0033427 | 0.025627 |  | 1 | 0 | 0 | 0
SD | 1487.2143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 469.2143 | 3.5961 | 0.020563 | 0.0034456 | 0.026416 |  | 1 | 0 | 0 | 0
SF | 1492.0643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 474.0643 | 2.3541 | 0.0087217 | 0.0014598 | 0.011192 |  | 0 | 1 | 0 | 0
SF | 1505.6143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 487.6143 | 2.4214 | 0.008971 | 0.0014972 | 0.011479 |  | 0 | 1 | 0 | 0
SD | 1510.4643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 492.4643 | 3.7743 | 0.021582 | 0.0035984 | 0.027588 |  | 1 | 0 | 0 | 0
SD | 1526.1143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 508.1143 | 3.8943 | 0.022268 | 0.0037013 | 0.028377 |  | 1 | 0 | 0 | 0
SF | 1530.9643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 512.9643 | 2.5472 | 0.0094374 | 0.0015672 | 0.012015 |  | 0 | 1 | 0 | 0
SF | 1544.5143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 526.5143 | 2.6145 | 0.0096867 | 0.0016046 | 0.012302 |  | 0 | 1 | 0 | 0
SD | 1549.3643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 531.3643 | 4.0724 | 0.023287 | 0.0038541 | 0.029548 |  | 1 | 0 | 0 | 0
SD | 1565.0143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 547.0143 | 4.1924 | 0.023973 | 0.003957 | 0.030337 |  | 1 | 0 | 0 | 0
SF | 1569.8643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 551.8643 | 2.7404 | 0.010153 | 0.0016745 | 0.012838 |  | 0 | 1 | 0 | 0
SF | 1583.4143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 565.4143 | 2.8077 | 0.010402 | 0.0017119 | 0.013125 |  | 0 | 1 | 0 | 0
SD | 1588.2643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 570.2643 | 4.3706 | 0.024992 | 0.0041099 | 0.031509 |  | 1 | 0 | 0 | 0
SD | 1603.9143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 585.9143 | 4.4905 | 0.025678 | 0.0042127 | 0.032298 |  | 1 | 0 | 0 | 0
SF | 1608.7643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 590.7643 | 2.9336 | 0.010869 | 0.0017819 | 0.013661 |  | 0 | 1 | 0 | 0
SF | 1622.3143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 604.3143 | 3.0009 | 0.011118 | 0.0018193 | 0.013948 |  | 0 | 1 | 0 | 0
SD | 1627.1643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 609.1643 | 4.6687 | 0.026697 | 0.0043656 | 0.033469 |  | 1 | 0 | 0 | 0
SD | 1642.8143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 624.8143 | 4.7887 | 0.027383 | 0.0044685 | 0.034258 |  | 1 | 0 | 0 | 0
SF | 1647.6643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 629.6643 | 3.1267 | 0.011584 | 0.0018892 | 0.014484 |  | 0 | 1 | 0 | 0
SF | 1661.2143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 643.2143 | 3.194 | 0.011834 | 0.0019266 | 0.014771 |  | 0 | 1 | 0 | 0
SD | 1666.0643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 648.0643 | 4.9668 | 0.028402 | 0.0046213 | 0.03543 |  | 1 | 0 | 0 | 0
SD | 1681.7143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 652.2857 | 4.9992 | 0.028587 | 0.004649 | 0.035643 |  | 1 | 0 | 0 | 0
SF | 1686.5643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 647.4357 | 3.215 | 0.011911 | 0.0019383 | 0.01486 |  | 0 | 1 | 0 | 0
SF | 1700.1143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 633.8857 | 3.1477 | 0.011662 | 0.0019009 | 0.014573 |  | 0 | 1 | 0 | 0
SD | 1704.9643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 629.0357 | 4.821 | 0.027568 | 0.0044962 | 0.034471 |  | 1 | 0 | 0 | 0
SD | 1720.6143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 613.3857 | 4.7011 | 0.026882 | 0.0043933 | 0.033682 |  | 1 | 0 | 0 | 0
SF | 1725.4643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 608.5357 | 3.0218 | 0.011196 | 0.0018309 | 0.014037 |  | 0 | 1 | 0 | 0
SF | 1739.0143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 594.9857 | 2.9545 | 0.010946 | 0.0017935 | 0.01375 |  | 0 | 1 | 0 | 0
SD | 1743.8643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 590.1357 | 4.5229 | 0.025863 | 0.0042405 | 0.03251 |  | 1 | 0 | 0 | 0
SD | 1759.5143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 574.4857 | 4.4029 | 0.025177 | 0.0041376 | 0.031722 |  | 1 | 0 | 0 | 0
SF | 1764.3643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 569.6357 | 2.8286 | 0.01048 | 0.0017236 | 0.013214 |  | 0 | 1 | 0 | 0
SF | 1777.9143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 556.0857 | 2.7614 | 0.010231 | 0.0016862 | 0.012927 |  | 0 | 1 | 0 | 0
SD | 1782.7643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 551.2357 | 4.2247 | 0.024158 | 0.0039848 | 0.03055 |  | 1 | 0 | 0 | 0
SD | 1798.4143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 535.5857 | 4.1048 | 0.023472 | 0.0038819 | 0.029761 |  | 1 | 0 | 0 | 0
SF | 1803.2643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 530.7357 | 2.6355 | 0.0097643 | 0.0016162 | 0.012391 |  | 0 | 1 | 0 | 0
SF | 1816.8143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 517.1857 | 2.5682 | 0.009515 | 0.0015788 | 0.012104 |  | 0 | 1 | 0 | 0
SD | 1821.6643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 512.3357 | 3.9266 | 0.022453 | 0.003729 | 0.028589 |  | 1 | 0 | 0 | 0
SD | 1837.3143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 496.6857 | 3.8067 | 0.021767 | 0.0036262 | 0.027801 |  | 1 | 0 | 0 | 0
SF | 1842.1643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 491.8357 | 2.4423 | 0.0090487 | 0.0015089 | 0.011568 |  | 0 | 1 | 0 | 0
SF | 1855.7143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 478.2857 | 2.375 | 0.0087994 | 0.0014715 | 0.011281 |  | 0 | 1 | 0 | 0
SD | 1860.5643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 473.4357 | 3.6285 | 0.020748 | 0.0034733 | 0.026629 |  | 1 | 0 | 0 | 0
SD | 1876.2143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 457.7857 | 3.5085 | 0.020063 | 0.0033704 | 0.02584 |  | 1 | 0 | 0 | 0
SF | 1881.0643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 452.9357 | 2.2491 | 0.008333 | 0.0014015 | 0.010745 |  | 0 | 1 | 0 | 0
SF | 1894.6143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 439.3857 | 2.1819 | 0.0080837 | 0.0013641 | 0.010458 |  | 0 | 1 | 0 | 0
SD | 1899.4643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 434.5357 | 3.3303 | 0.019044 | 0.0032176 | 0.024668 |  | 1 | 0 | 0 | 0
SD | 1915.1143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 418.8857 | 3.2104 | 0.018358 | 0.0031147 | 0.02388 |  | 1 | 0 | 0 | 0
SF | 1919.9643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 414.0357 | 2.056 | 0.0076173 | 0.0012942 | 0.0099219 |  | 0 | 1 | 0 | 0
SF | 1933.5143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 400.4857 | 1.9887 | 0.007368 | 0.0012568 | 0.0096352 |  | 0 | 1 | 0 | 0
SD | 1938.3643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 395.6357 | 3.0322 | 0.017339 | 0.0029619 | 0.022708 |  | 1 | 0 | 0 | 0
SD | 1954.0143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 379.9857 | 2.9123 | 0.016653 | 0.002859 | 0.021919 |  | 1 | 0 | 0 | 0
SF | 1958.8643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 375.1357 | 1.8628 | 0.0069016 | 0.0011868 | 0.0090989 |  | 0 | 1 | 0 | 0
SF | 1972.4143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 361.5857 | 1.7955 | 0.0066524 | 0.0011494 | 0.0088122 |  | 0 | 1 | 0 | 0
SD | 1977.2643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 356.7357 | 2.7341 | 0.015634 | 0.0027062 | 0.020747 |  | 1 | 0 | 0 | 0
SD | 1992.9143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 341.0857 | 2.6141 | 0.014948 | 0.0026033 | 0.019958 |  | 1 | 0 | 0 | 0
SF | 1997.7643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 336.2357 | 1.6696 | 0.006186 | 0.0010795 | 0.0082759 |  | 0 | 1 | 0 | 0
SF | 2011.3143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 322.6857 | 1.6024 | 0.0059367 | 0.0010421 | 0.0079892 |  | 0 | 1 | 0 | 0
SD | 2016.1643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 317.8357 | 2.4359 | 0.013929 | 0.0024504 | 0.018787 |  | 1 | 0 | 0 | 0
SD | 2031.8143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 302.1857 | 2.316 | 0.013243 | 0.0023476 | 0.017998 |  | 1 | 0 | 0 | 0
SF | 2036.6643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 297.3357 | 1.4765 | 0.0054703 | 0.00097211 | 0.0074528 |  | 0 | 1 | 0 | 0
SF | 2050.2143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 283.7857 | 1.4092 | 0.005221 | 0.00093472 | 0.0071662 |  | 0 | 1 | 0 | 0
SD | 2055.0643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 278.9357 | 2.1378 | 0.012224 | 0.0021947 | 0.016826 |  | 1 | 0 | 0 | 0
SD1 | 2070.7143 | 0.25 | 0 | 0 | 0 | 0 | 263.2857 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1 | 0
SF1 | 2075.5643 | 0.25 | 0 | 0 | 0 | 0 | 258.4357 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1
SF1 | 2336.3383 | 0.25 | 0 | 0 | 0 | 0 | 2.3383 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1
SD1 | 2341.1883 | 0.25 | 0 | 0 | 0 | 0 | 7.1883 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1 | 0
SD | 2356.8383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 22.8383 | 0.17504 | 0.0010009 | 0.00051118 | 0.003919 |  | 1 | 0 | 0 | 0
SF | 2361.6883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 27.6883 | 0.13749 | 0.0005094 | 0.00022798 | 0.0017478 |  | 0 | 1 | 0 | 0
SF | 2375.2383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 41.2383 | 0.20478 | 0.00075869 | 0.00026537 | 0.0020345 |  | 0 | 1 | 0 | 0
SD | 2380.0883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 46.0883 | 0.35323 | 0.0020198 | 0.00066402 | 0.0050908 |  | 1 | 0 | 0 | 0
SD | 2395.7383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 61.7383 | 0.47317 | 0.0027057 | 0.0007669 | 0.0058796 |  | 1 | 0 | 0 | 0
SF | 2400.5883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 66.5883 | 0.33066 | 0.0012251 | 0.00033533 | 0.0025708 |  | 0 | 1 | 0 | 0
SF | 2414.1383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 80.1383 | 0.39794 | 0.0014744 | 0.00037272 | 0.0028575 |  | 0 | 1 | 0 | 0
SD | 2418.9883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 84.9883 | 0.65136 | 0.0037246 | 0.00091974 | 0.0070514 |  | 1 | 0 | 0 | 0
SD | 2434.6383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 100.6383 | 0.7713 | 0.0044105 | 0.0010226 | 0.0078401 |  | 1 | 0 | 0 | 0
SF | 2439.4883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 105.4883 | 0.52382 | 0.0019407 | 0.00044268 | 0.0033939 |  | 0 | 1 | 0 | 0
SF | 2453.0383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 119.0383 | 0.59111 | 0.00219 | 0.00048007 | 0.0036805 |  | 0 | 1 | 0 | 0
SD | 2457.8883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 123.8883 | 0.9495 | 0.0054295 | 0.0011755 | 0.0090119 |  | 1 | 0 | 0 | 0
SD | 2473.5383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 139.5383 | 1.0694 | 0.0061153 | 0.0012783 | 0.0098006 |  | 1 | 0 | 0 | 0
SF | 2478.3883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 144.3883 | 0.71699 | 0.0026564 | 0.00055003 | 0.0042169 |  | 0 | 1 | 0 | 0
SF | 2491.9383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 157.9383 | 0.78428 | 0.0029057 | 0.00058742 | 0.0045036 |  | 0 | 1 | 0 | 0
SD | 2496.7883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 162.7883 | 1.2476 | 0.0071343 | 0.0014312 | 0.010972 |  | 1 | 0 | 0 | 0
SD | 2512.4383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 178.4383 | 1.3676 | 0.0078201 | 0.0015341 | 0.011761 |  | 1 | 0 | 0 | 0
SF | 2517.2883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 183.2883 | 0.91016 | 0.0033721 | 0.00065738 | 0.0050399 |  | 0 | 1 | 0 | 0
SF | 2530.8383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 196.8383 | 0.97744 | 0.0036214 | 0.00069477 | 0.0053266 |  | 0 | 1 | 0 | 0
SD | 2535.6883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 201.6883 | 1.5458 | 0.0088391 | 0.0016869 | 0.012933 |  | 1 | 0 | 0 | 0
SD | 2551.3383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 217.3383 | 1.6657 | 0.0095249 | 0.0017898 | 0.013722 |  | 1 | 0 | 0 | 0
SF | 2556.1883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 222.1883 | 1.1033 | 0.0040878 | 0.00076473 | 0.0058629 |  | 0 | 1 | 0 | 0
SF | 2569.7383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 235.7383 | 1.1706 | 0.004337 | 0.00080212 | 0.0061496 |  | 0 | 1 | 0 | 0
SD | 2574.5883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 240.5883 | 1.8439 | 0.010544 | 0.0019426 | 0.014893 |  | 1 | 0 | 0 | 0
SD | 2590.2383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 256.2383 | 1.9638 | 0.01123 | 0.0020455 | 0.015682 |  | 1 | 0 | 0 | 0
SF | 2595.0883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 261.0883 | 1.2965 | 0.0048034 | 0.00087208 | 0.0066859 |  | 0 | 1 | 0 | 0
SF | 2608.6383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 274.6383 | 1.3638 | 0.0050527 | 0.00090947 | 0.0069726 |  | 0 | 1 | 0 | 0
SD | 2613.4883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 279.4883 | 2.142 | 0.012249 | 0.0021983 | 0.016854 |  | 1 | 0 | 0 | 0
SD | 2629.1383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 295.1383 | 2.262 | 0.012935 | 0.0023012 | 0.017643 |  | 1 | 0 | 0 | 0
SF | 2633.9883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 299.9883 | 1.4897 | 0.0055191 | 0.00097943 | 0.007509 |  | 0 | 1 | 0 | 0
SF | 2647.5383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 313.5383 | 1.5569 | 0.0057684 | 0.0010168 | 0.0077956 |  | 0 | 1 | 0 | 0
SD | 2652.3883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 318.3883 | 2.4402 | 0.013953 | 0.0024541 | 0.018815 |  | 1 | 0 | 0 | 0
SD | 2668.0383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 334.0383 | 2.5601 | 0.014639 | 0.0025569 | 0.019603 |  | 1 | 0 | 0 | 0
SF | 2672.8883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 338.8883 | 1.6828 | 0.0062348 | 0.0010868 | 0.008332 |  | 0 | 1 | 0 | 0
SF | 2686.4383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 352.4383 | 1.7501 | 0.0064841 | 0.0011242 | 0.0086187 |  | 0 | 1 | 0 | 0
SD | 2691.2883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 357.2883 | 2.7383 | 0.015658 | 0.0027098 | 0.020775 |  | 1 | 0 | 0 | 0
SD | 2706.9383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 372.9383 | 2.8582 | 0.016344 | 0.0028127 | 0.021564 |  | 1 | 0 | 0 | 0
SF | 2711.7883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 377.7883 | 1.876 | 0.0069504 | 0.0011941 | 0.009155 |  | 0 | 1 | 0 | 0
SF | 2725.3383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 391.3383 | 1.9433 | 0.0071997 | 0.0012315 | 0.0094417 |  | 0 | 1 | 0 | 0
SD | 2730.1883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 396.1883 | 3.0364 | 0.017363 | 0.0029655 | 0.022736 |  | 1 | 0 | 0 | 0
SD | 2745.8383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 411.8383 | 3.1564 | 0.018049 | 0.0030684 | 0.023524 |  | 1 | 0 | 0 | 0
SF | 2750.6883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 416.6883 | 2.0692 | 0.0076661 | 0.0013015 | 0.009978 |  | 0 | 1 | 0 | 0
SF | 2764.2383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 430.2383 | 2.1364 | 0.0079154 | 0.0013389 | 0.010265 |  | 0 | 1 | 0 | 0
SD | 2769.0883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 435.0883 | 3.3346 | 0.019068 | 0.0032212 | 0.024696 |  | 1 | 0 | 0 | 0
SD | 2784.7383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 450.7383 | 3.4545 | 0.019754 | 0.0033241 | 0.025485 |  | 1 | 0 | 0 | 0
SF | 2789.5883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 455.5883 | 2.2623 | 0.0083818 | 0.0014088 | 0.010801 |  | 0 | 1 | 0 | 0
SF | 2803.1383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 469.1383 | 2.3296 | 0.0086311 | 0.0014462 | 0.011088 |  | 0 | 1 | 0 | 0
SD | 2807.9883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 473.9883 | 3.6327 | 0.020773 | 0.003477 | 0.026657 |  | 1 | 0 | 0 | 0
SD | 2823.6383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 489.6383 | 3.7526 | 0.021459 | 0.0035798 | 0.027445 |  | 1 | 0 | 0 | 0
SF | 2828.4883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 494.4883 | 2.4555 | 0.0090975 | 0.0015162 | 0.011624 |  | 0 | 1 | 0 | 0
SF | 2842.0383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 508.0383 | 2.5228 | 0.0093467 | 0.0015536 | 0.011911 |  | 0 | 1 | 0 | 0
SD | 2846.8883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 512.8883 | 3.9308 | 0.022478 | 0.0037327 | 0.028617 |  | 1 | 0 | 0 | 0
SD | 2862.5383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 528.5383 | 4.0508 | 0.023163 | 0.0038356 | 0.029406 |  | 1 | 0 | 0 | 0
SF | 2867.3883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 533.3883 | 2.6487 | 0.0098131 | 0.0016235 | 0.012447 |  | 0 | 1 | 0 | 0
SF | 2880.9383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 546.9383 | 2.7159 | 0.010062 | 0.0016609 | 0.012734 |  | 0 | 1 | 0 | 0
SD | 2885.7883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 551.7883 | 4.229 | 0.024182 | 0.0039884 | 0.030578 |  | 1 | 0 | 0 | 0
SD | 2901.4383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 567.4383 | 4.3489 | 0.024868 | 0.0040913 | 0.031366 |  | 1 | 0 | 0 | 0
SF | 2906.2883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 572.2883 | 2.8418 | 0.010529 | 0.0017309 | 0.01327 |  | 0 | 1 | 0 | 0
SF | 2919.8383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 585.8383 | 2.9091 | 0.010778 | 0.0017683 | 0.013557 |  | 0 | 1 | 0 | 0
SD | 2924.6883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 590.6883 | 4.5271 | 0.025887 | 0.0042441 | 0.032538 |  | 1 | 0 | 0 | 0
SD | 2940.3383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 606.3383 | 4.6471 | 0.026573 | 0.004347 | 0.033327 |  | 1 | 0 | 0 | 0
SF | 2945.1883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 611.1883 | 3.035 | 0.011244 | 0.0018382 | 0.014093 |  | 0 | 1 | 0 | 0
SF | 2958.7383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 624.7383 | 3.1023 | 0.011494 | 0.0018756 | 0.01438 |  | 0 | 1 | 0 | 0
SD | 2963.5883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 629.5883 | 4.8252 | 0.027592 | 0.0044998 | 0.034499 |  | 1 | 0 | 0 | 0
SD | 2979.2383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 645.2383 | 4.9452 | 0.028278 | 0.0046027 | 0.035287 |  | 1 | 0 | 0 | 0
SF | 2984.0883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 650.0883 | 3.2282 | 0.01196 | 0.0019456 | 0.014916 |  | 0 | 1 | 0 | 0
SF | 2997.6383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 663.6383 | 3.2954 | 0.012209 | 0.001983 | 0.015203 |  | 0 | 1 | 0 | 0
SD | 3002.4883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 668.4883 | 5.1234 | 0.029297 | 0.0047556 | 0.036459 |  | 1 | 0 | 0 | 0
SD | 3018.1383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 684.1383 | 5.2433 | 0.029983 | 0.0048584 | 0.037248 |  | 1 | 0 | 0 | 0
SF | 3022.9883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 688.9883 | 3.4213 | 0.012676 | 0.0020529 | 0.015739 |  | 0 | 1 | 0 | 0
SF | 3036.5383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 702.5383 | 3.4886 | 0.012925 | 0.0020903 | 0.016026 |  | 0 | 1 | 0 | 0
SD | 3041.3883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 707.3883 | 5.4215 | 0.031002 | 0.0050113 | 0.03842 |  | 1 | 0 | 0 | 0
SD | 3057.0383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 723.0383 | 5.5415 | 0.031687 | 0.0051142 | 0.039209 |  | 1 | 0 | 0 | 0
SF | 3061.8883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 727.8883 | 3.6145 | 0.013391 | 0.0021603 | 0.016562 |  | 0 | 1 | 0 | 0
SF | 3075.4383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 741.4383 | 3.6818 | 0.013641 | 0.0021977 | 0.016849 |  | 0 | 1 | 0 | 0
SD | 3080.2883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 746.2883 | 5.7196 | 0.032706 | 0.005267 | 0.04038 |  | 1 | 0 | 0 | 0
SD | 3095.9383 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 761.9383 | 5.8396 | 0.033392 | 0.0053699 | 0.041169 |  | 1 | 0 | 0 | 0
SF | 3100.7883 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 766.7883 | 3.8077 | 0.014107 | 0.0022676 | 0.017385 |  | 0 | 1 | 0 | 0
SF | 3114.3383 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 780.3383 | 3.8749 | 0.014356 | 0.002305 | 0.017672 |  | 0 | 1 | 0 | 0
SD | 3119.1883 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 785.1883 | 6.0178 | 0.034411 | 0.0055227 | 0.042341 |  | 1 | 0 | 0 | 0
SD1 | 3134.8383 | 0.25 | 0 | 0 | 0 | 0 | 800.8383 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1 | 0
SF1 | 3139.6883 | 0.25 | 0 | 0 | 0 | 0 | 805.6883 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1
SF1 | 3555.619 | 0.25 | 0 | 0 | 0 | 0 | 814.381 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1
SD1 | 3560.469 | 0.25 | 0 | 0 | 0 | 0 | 809.531 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1 | 0
SD | 3576.119 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 793.881 | 6.0844 | 0.034792 | 0.0055799 | 0.042779 |  | 1 | 0 | 0 | 0
SF | 3580.969 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 789.031 | 3.9181 | 0.014516 | 0.002329 | 0.017856 |  | 0 | 1 | 0 | 0
SF | 3594.519 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 775.481 | 3.8508 | 0.014267 | 0.0022916 | 0.017569 |  | 0 | 1 | 0 | 0
SD | 3599.369 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 770.631 | 5.9062 | 0.033773 | 0.005427 | 0.041607 |  | 1 | 0 | 0 | 0
SD | 3615.019 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 754.981 | 5.7863 | 0.033087 | 0.0053241 | 0.040818 |  | 1 | 0 | 0 | 0
SF | 3619.869 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 750.131 | 3.7249 | 0.013801 | 0.0022217 | 0.017033 |  | 0 | 1 | 0 | 0
SF | 3633.419 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 736.581 | 3.6576 | 0.013551 | 0.0021843 | 0.016746 |  | 0 | 1 | 0 | 0
SD | 3638.269 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 731.731 | 5.6081 | 0.032068 | 0.0051713 | 0.039647 |  | 1 | 0 | 0 | 0
SD | 3653.919 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 716.081 | 5.4881 | 0.031383 | 0.0050684 | 0.038858 |  | 1 | 0 | 0 | 0
SF | 3658.769 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 711.231 | 3.5318 | 0.013085 | 0.0021143 | 0.01621 |  | 0 | 1 | 0 | 0
SF | 3672.319 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 697.681 | 3.4645 | 0.012836 | 0.0020769 | 0.015923 |  | 0 | 1 | 0 | 0
SD | 3677.169 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 692.831 | 5.3099 | 0.030364 | 0.0049156 | 0.037686 |  | 1 | 0 | 0 | 0
SD | 3692.819 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 677.181 | 5.19 | 0.029678 | 0.0048127 | 0.036897 |  | 1 | 0 | 0 | 0
SF | 3697.669 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 672.331 | 3.3386 | 0.012369 | 0.002007 | 0.015387 |  | 0 | 1 | 0 | 0
SF | 3711.219 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 658.781 | 3.2713 | 0.01212 | 0.0019696 | 0.0151 |  | 0 | 1 | 0 | 0
SD | 3716.069 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 653.931 | 5.0118 | 0.028659 | 0.0046599 | 0.035726 |  | 1 | 0 | 0 | 0
SD | 3731.719 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 638.281 | 4.8919 | 0.027973 | 0.004557 | 0.034937 |  | 1 | 0 | 0 | 0
SF | 3736.569 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 633.431 | 3.1454 | 0.011654 | 0.0018996 | 0.014564 |  | 0 | 1 | 0 | 0
SF | 3750.119 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 619.881 | 3.0782 | 0.011404 | 0.0018622 | 0.014277 |  | 0 | 1 | 0 | 0
SD | 3754.969 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 615.031 | 4.7137 | 0.026954 | 0.0044041 | 0.033765 |  | 1 | 0 | 0 | 0
SD | 3770.619 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 599.381 | 4.5937 | 0.026268 | 0.0043013 | 0.032976 |  | 1 | 0 | 0 | 0
SF | 3775.469 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 594.531 | 2.9523 | 0.010938 | 0.0017923 | 0.013741 |  | 0 | 1 | 0 | 0
SF | 3789.019 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 580.981 | 2.885 | 0.010689 | 0.0017549 | 0.013454 |  | 0 | 1 | 0 | 0
SD | 3793.869 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 576.131 | 4.4155 | 0.025249 | 0.0041484 | 0.031805 |  | 1 | 0 | 0 | 0
SD | 3809.519 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 560.481 | 4.2956 | 0.024563 | 0.0040455 | 0.031016 |  | 1 | 0 | 0 | 0
SF | 3814.369 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 555.631 | 2.7591 | 0.010222 | 0.0016849 | 0.012918 |  | 0 | 1 | 0 | 0
SF | 3827.919 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 542.081 | 2.6918 | 0.0099731 | 0.0016475 | 0.012631 |  | 0 | 1 | 0 | 0
SD | 3832.769 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 537.231 | 4.1174 | 0.023544 | 0.0038927 | 0.029844 |  | 1 | 0 | 0 | 0
SD | 3848.419 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 521.581 | 3.9975 | 0.022858 | 0.0037898 | 0.029055 |  | 1 | 0 | 0 | 0
SF | 3853.269 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 516.731 | 2.5659 | 0.0095067 | 0.0015776 | 0.012095 |  | 0 | 1 | 0 | 0
SF | 3866.819 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 503.181 | 2.4987 | 0.0092574 | 0.0015402 | 0.011808 |  | 0 | 1 | 0 | 0
SD | 3871.669 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 498.331 | 3.8193 | 0.02184 | 0.003637 | 0.027883 |  | 1 | 0 | 0 | 0
SD | 3887.319 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 482.681 | 3.6993 | 0.021154 | 0.0035341 | 0.027095 |  | 1 | 0 | 0 | 0
SF | 3892.169 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 477.831 | 2.3728 | 0.008791 | 0.0014702 | 0.011272 |  | 0 | 1 | 0 | 0
SF | 3905.719 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 464.281 | 2.3055 | 0.0085417 | 0.0014328 | 0.010985 |  | 0 | 1 | 0 | 0
SD | 3910.569 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 459.431 | 3.5211 | 0.020135 | 0.0033813 | 0.025923 |  | 1 | 0 | 0 | 0
SD | 3926.219 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 443.781 | 3.4012 | 0.019449 | 0.0032784 | 0.025134 |  | 1 | 0 | 0 | 0
SF | 3931.069 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 438.931 | 2.1796 | 0.0080753 | 0.0013629 | 0.010449 |  | 0 | 1 | 0 | 0
SF | 3944.619 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 425.381 | 2.1123 | 0.007826 | 0.0013255 | 0.010162 |  | 0 | 1 | 0 | 0
SD | 3949.469 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 420.531 | 3.223 | 0.01843 | 0.0031255 | 0.023962 |  | 1 | 0 | 0 | 0
SD | 3965.119 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 404.881 | 3.1031 | 0.017744 | 0.0030227 | 0.023174 |  | 1 | 0 | 0 | 0
SF | 3969.969 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 400.031 | 1.9864 | 0.0073597 | 0.0012555 | 0.0096256 |  | 0 | 1 | 0 | 0
SF | 3983.519 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 386.481 | 1.9192 | 0.0071104 | 0.0012181 | 0.0093389 |  | 0 | 1 | 0 | 0
SD | 3988.369 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 381.631 | 2.9249 | 0.016725 | 0.0028698 | 0.022002 |  | 1 | 0 | 0 | 0
SD | 4004.019 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 365.981 | 2.8049 | 0.016039 | 0.0027669 | 0.021213 |  | 1 | 0 | 0 | 0
SF | 4008.869 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 361.131 | 1.7933 | 0.006644 | 0.0011482 | 0.0088026 |  | 0 | 1 | 0 | 0
SF | 4022.419 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 347.581 | 1.726 | 0.0063947 | 0.0011108 | 0.0085159 |  | 0 | 1 | 0 | 0
SD | 4027.269 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 342.731 | 2.6267 | 0.01502 | 0.0026141 | 0.020041 |  | 1 | 0 | 0 | 0
SD | 4042.919 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 327.081 | 2.5068 | 0.014334 | 0.0025112 | 0.019253 |  | 1 | 0 | 0 | 0
SF | 4047.769 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 322.231 | 1.6001 | 0.0059283 | 0.0010408 | 0.0079796 |  | 0 | 1 | 0 | 0
SF | 4061.319 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 308.681 | 1.5328 | 0.005679 | 0.0010034 | 0.0076929 |  | 0 | 1 | 0 | 0
SD | 4066.169 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 303.831 | 2.3286 | 0.013316 | 0.0023584 | 0.018081 |  | 1 | 0 | 0 | 0
SD | 4081.819 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 288.181 | 2.2087 | 0.01263 | 0.0022555 | 0.017292 |  | 1 | 0 | 0 | 0
SF | 4086.669 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 283.331 | 1.4069 | 0.0052126 | 0.00093346 | 0.0071565 |  | 0 | 1 | 0 | 0
SF | 4100.219 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 269.781 | 1.3397 | 0.0049634 | 0.00089607 | 0.0068699 |  | 0 | 1 | 0 | 0
SD | 4105.069 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 264.931 | 2.0305 | 0.011611 | 0.0021026 | 0.01612 |  | 1 | 0 | 0 | 0
SD | 4120.719 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 249.281 | 1.9105 | 0.010925 | 0.0019998 | 0.015332 |  | 1 | 0 | 0 | 0
SF | 4125.569 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 244.431 | 1.2138 | 0.004497 | 0.00082611 | 0.0063335 |  | 0 | 1 | 0 | 0
SF | 4139.119 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 230.881 | 1.1465 | 0.0042477 | 0.00078872 | 0.0060468 |  | 0 | 1 | 0 | 0
SD | 4143.969 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 226.031 | 1.7323 | 0.0099059 | 0.0018469 | 0.01416 |  | 1 | 0 | 0 | 0
SD | 4159.619 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 210.381 | 1.6124 | 0.00922 | 0.001744 | 0.013371 |  | 1 | 0 | 0 | 0
SF | 4164.469 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 205.531 | 1.0206 | 0.0037813 | 0.00071876 | 0.0055105 |  | 0 | 1 | 0 | 0
SF | 4178.019 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 191.981 | 0.95332 | 0.003532 | 0.00068137 | 0.0052238 |  | 0 | 1 | 0 | 0
SD | 4182.869 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 187.131 | 1.4342 | 0.0082011 | 0.0015912 | 0.012199 |  | 1 | 0 | 0 | 0
SD | 4198.519 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 171.481 | 1.3143 | 0.0075152 | 0.0014883 | 0.011411 |  | 1 | 0 | 0 | 0
SF | 4203.369 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 166.631 | 0.82744 | 0.0030656 | 0.00061141 | 0.0046875 |  | 0 | 1 | 0 | 0
SF | 4216.919 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 153.081 | 0.76016 | 0.0028163 | 0.00057402 | 0.0044008 |  | 0 | 1 | 0 | 0
SD | 4221.769 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 148.231 | 1.1361 | 0.0064963 | 0.0013355 | 0.010239 |  | 1 | 0 | 0 | 0
SD | 4237.419 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 132.581 | 1.0161 | 0.0058104 | 0.0012326 | 0.00945 |  | 1 | 0 | 0 | 0
SF | 4242.269 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 127.731 | 0.63428 | 0.00235 | 0.00050406 | 0.0038645 |  | 0 | 1 | 0 | 0
SF | 4255.819 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 114.181 | 0.56699 | 0.0021007 | 0.00046667 | 0.0035778 |  | 0 | 1 | 0 | 0
SD | 4260.669 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 109.331 | 0.83793 | 0.0047915 | 0.0010798 | 0.0082782 |  | 1 | 0 | 0 | 0
SD | 4276.319 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 93.681 | 0.71798 | 0.0041056 | 0.00097689 | 0.0074895 |  | 1 | 0 | 0 | 0
SF | 4281.169 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 88.831 | 0.44111 | 0.0016343 | 0.00039671 | 0.0030414 |  | 0 | 1 | 0 | 0
SF | 4294.719 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 75.281 | 0.37382 | 0.001385 | 0.00035931 | 0.0027547 |  | 0 | 1 | 0 | 0
SD | 4299.569 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 70.431 | 0.53979 | 0.0030867 | 0.00082404 | 0.0063177 |  | 1 | 0 | 0 | 0
SD | 4315.219 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 54.781 | 0.41985 | 0.0024008 | 0.00072116 | 0.0055289 |  | 1 | 0 | 0 | 0
SF | 4320.069 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 49.931 | 0.24794 | 0.00091862 | 0.00028936 | 0.0022184 |  | 0 | 1 | 0 | 0
SF | 4333.619 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 36.381 | 0.18066 | 0.00066933 | 0.00025196 | 0.0019317 |  | 0 | 1 | 0 | 0
SD | 4338.469 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 31.531 | 0.24166 | 0.0013819 | 0.00056832 | 0.0043571 |  | 1 | 0 | 0 | 0
SD1 | 4354.119 | 0.25 | 0 | 0 | 0 | 0 | 15.881 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1 | 0
SF1 | 4358.969 | 0.25 | 0 | 0 | 0 | 0 | 11.031 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1
SF1 | 4619.743 | 0.25 | 0 | 0 | 0 | 0 | 249.743 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1
SD1 | 4624.593 | 0.25 | 0 | 0 | 0 | 0 | 254.593 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1 | 0
SD | 4640.243 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 270.243 | 2.0712 | 0.011844 | 0.0021376 | 0.016388 |  | 1 | 0 | 0 | 0
SF | 4645.093 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 275.093 | 1.366 | 0.0050611 | 0.00091073 | 0.0069822 |  | 0 | 1 | 0 | 0
SF | 4658.643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 288.643 | 1.4333 | 0.0053104 | 0.00094812 | 0.0072689 |  | 0 | 1 | 0 | 0
SD | 4663.493 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 293.493 | 2.2494 | 0.012862 | 0.0022904 | 0.01756 |  | 1 | 0 | 0 | 0
SD | 4679.143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 309.143 | 2.3693 | 0.013548 | 0.0023933 | 0.018349 |  | 1 | 0 | 0 | 0
SF | 4683.993 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 313.993 | 1.5592 | 0.0057768 | 0.0010181 | 0.0078053 |  | 0 | 1 | 0 | 0
SF | 4697.543 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 327.543 | 1.6265 | 0.006026 | 0.0010555 | 0.008092 |  | 0 | 1 | 0 | 0
SD | 4702.393 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 332.393 | 2.5475 | 0.014567 | 0.0025461 | 0.01952 |  | 1 | 0 | 0 | 0
SD | 4718.043 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 348.043 | 2.6674 | 0.015253 | 0.002649 | 0.020309 |  | 1 | 0 | 0 | 0
SF | 4722.893 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 352.893 | 1.7524 | 0.0064924 | 0.0011254 | 0.0086283 |  | 0 | 1 | 0 | 0
SF | 4736.443 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 366.443 | 1.8197 | 0.0067417 | 0.0011628 | 0.008915 |  | 0 | 1 | 0 | 0
SD | 4741.293 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 371.293 | 2.8456 | 0.016272 | 0.0028019 | 0.021481 |  | 1 | 0 | 0 | 0
SD | 4756.943 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 386.943 | 2.9656 | 0.016958 | 0.0029047 | 0.02227 |  | 1 | 0 | 0 | 0
SF | 4761.793 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 391.793 | 1.9455 | 0.0072081 | 0.0012328 | 0.0094513 |  | 0 | 1 | 0 | 0
SF | 4775.343 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 405.343 | 2.0128 | 0.0074574 | 0.0012702 | 0.009738 |  | 0 | 1 | 0 | 0
SD | 4780.193 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 410.193 | 3.1438 | 0.017977 | 0.0030576 | 0.023441 |  | 1 | 0 | 0 | 0
SD | 4795.843 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 425.843 | 3.2637 | 0.018663 | 0.0031605 | 0.02423 |  | 1 | 0 | 0 | 0
SF | 4800.693 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 430.693 | 2.1387 | 0.0079238 | 0.0013401 | 0.010274 |  | 0 | 1 | 0 | 0
SF | 4814.243 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 444.243 | 2.206 | 0.0081731 | 0.0013775 | 0.010561 |  | 0 | 1 | 0 | 0
SD | 4819.093 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 449.093 | 3.4419 | 0.019682 | 0.0033133 | 0.025402 |  | 1 | 0 | 0 | 0
SD | 4834.743 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 464.743 | 3.5618 | 0.020368 | 0.0034162 | 0.026191 |  | 1 | 0 | 0 | 0
SF | 4839.593 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 469.593 | 2.3319 | 0.0086394 | 0.0014475 | 0.011097 |  | 0 | 1 | 0 | 0
SF | 4853.143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 483.143 | 2.3991 | 0.0088887 | 0.0014849 | 0.011384 |  | 0 | 1 | 0 | 0
SD | 4857.993 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 487.993 | 3.74 | 0.021386 | 0.003569 | 0.027362 |  | 1 | 0 | 0 | 0
SD | 4873.643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 503.643 | 3.86 | 0.022072 | 0.0036719 | 0.028151 |  | 1 | 0 | 0 | 0
SF | 4878.493 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 508.493 | 2.525 | 0.0093551 | 0.0015548 | 0.01192 |  | 0 | 1 | 0 | 0
SF | 4892.043 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 522.043 | 2.5923 | 0.0096044 | 0.0015922 | 0.012207 |  | 0 | 1 | 0 | 0
SD | 4896.893 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 526.893 | 4.0382 | 0.023091 | 0.0038247 | 0.029323 |  | 1 | 0 | 0 | 0
SD | 4912.543 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 542.543 | 4.1581 | 0.023777 | 0.0039276 | 0.030112 |  | 1 | 0 | 0 | 0
SF | 4917.393 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 547.393 | 2.7182 | 0.010071 | 0.0016622 | 0.012743 |  | 0 | 1 | 0 | 0
SF | 4930.943 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 560.943 | 2.7855 | 0.01032 | 0.0016996 | 0.01303 |  | 0 | 1 | 0 | 0
SD | 4935.793 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 565.793 | 4.3363 | 0.024796 | 0.0040805 | 0.031284 |  | 1 | 0 | 0 | 0
SD | 4951.443 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 581.443 | 4.4563 | 0.025482 | 0.0041833 | 0.032072 |  | 1 | 0 | 0 | 0
SF | 4956.293 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 586.293 | 2.9114 | 0.010786 | 0.0017695 | 0.013566 |  | 0 | 1 | 0 | 0
SF | 4969.843 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 599.843 | 2.9786 | 0.011036 | 0.0018069 | 0.013853 |  | 0 | 1 | 0 | 0
SD | 4974.693 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 604.693 | 4.6344 | 0.026501 | 0.0043362 | 0.033244 |  | 1 | 0 | 0 | 0
SD | 4990.343 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 620.343 | 4.7544 | 0.027187 | 0.0044391 | 0.034033 |  | 1 | 0 | 0 | 0
SF | 4995.193 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 625.193 | 3.1045 | 0.011502 | 0.0018769 | 0.014389 |  | 0 | 1 | 0 | 0
SF | 5008.743 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 638.743 | 3.1718 | 0.011751 | 0.0019143 | 0.014676 |  | 0 | 1 | 0 | 0
SD | 5013.593 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 643.593 | 4.9326 | 0.028206 | 0.0045919 | 0.035205 |  | 1 | 0 | 0 | 0
SD | 5029.243 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 656.757 | 5.0335 | 0.028783 | 0.0046784 | 0.035868 |  | 1 | 0 | 0 | 0
SF | 5034.093 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 651.907 | 3.2372 | 0.011994 | 0.0019506 | 0.014955 |  | 0 | 1 | 0 | 0
SF | 5047.643 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 638.357 | 3.1699 | 0.011744 | 0.0019132 | 0.014668 |  | 0 | 1 | 0 | 0
SD | 5052.493 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 633.507 | 4.8553 | 0.027764 | 0.0045256 | 0.034696 |  | 1 | 0 | 0 | 0
SD | 5068.143 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 617.857 | 4.7353 | 0.027078 | 0.0044227 | 0.033907 |  | 1 | 0 | 0 | 0
SF | 5072.993 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 613.007 | 3.044 | 0.011278 | 0.0018433 | 0.014132 |  | 0 | 1 | 0 | 0
SF | 5086.543 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 599.457 | 2.9767 | 0.011029 | 0.0018059 | 0.013845 |  | 0 | 1 | 0 | 0
SD | 5091.393 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 594.607 | 4.5571 | 0.026059 | 0.0042699 | 0.032736 |  | 1 | 0 | 0 | 0
SD | 5107.043 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 578.957 | 4.4372 | 0.025373 | 0.004167 | 0.031947 |  | 1 | 0 | 0 | 0
SF | 5111.893 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 574.107 | 2.8509 | 0.010562 | 0.0017359 | 0.013309 |  | 0 | 1 | 0 | 0
SF | 5125.443 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 560.557 | 2.7836 | 0.010313 | 0.0016985 | 0.013022 |  | 0 | 1 | 0 | 0
SD | 5130.293 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 555.707 | 4.259 | 0.024354 | 0.0040142 | 0.030775 |  | 1 | 0 | 0 | 0
SD | 5145.943 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 540.057 | 4.1391 | 0.023668 | 0.0039113 | 0.029986 |  | 1 | 0 | 0 | 0
SF | 5150.793 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 535.207 | 2.6577 | 0.0098466 | 0.0016286 | 0.012486 |  | 0 | 1 | 0 | 0
SF | 5164.343 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 521.657 | 2.5904 | 0.0095973 | 0.0015912 | 0.012199 |  | 0 | 1 | 0 | 0
SD | 5169.193 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 516.807 | 3.9609 | 0.022649 | 0.0037584 | 0.028815 |  | 1 | 0 | 0 | 0
SD | 5184.843 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 501.157 | 3.8409 | 0.021963 | 0.0036556 | 0.028026 |  | 1 | 0 | 0 | 0
SF | 5189.693 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 496.307 | 2.4645 | 0.0091309 | 0.0015212 | 0.011663 |  | 0 | 1 | 0 | 0
SF | 5203.243 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 482.757 | 2.3972 | 0.0088816 | 0.0014838 | 0.011376 |  | 0 | 1 | 0 | 0
SD | 5208.093 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 477.907 | 3.6627 | 0.020944 | 0.0035027 | 0.026854 |  | 1 | 0 | 0 | 0
SD | 5223.743 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 462.257 | 3.5428 | 0.020259 | 0.0033998 | 0.026065 |  | 1 | 0 | 0 | 0
SF | 5228.593 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 457.407 | 2.2714 | 0.0084152 | 0.0014139 | 0.01084 |  | 0 | 1 | 0 | 0
SF | 5242.143 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 443.857 | 2.2041 | 0.008166 | 0.0013765 | 0.010553 |  | 0 | 1 | 0 | 0
SD | 5246.993 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 439.007 | 3.3646 | 0.01924 | 0.003247 | 0.024894 |  | 1 | 0 | 0 | 0
SD | 5262.643 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 423.357 | 3.2447 | 0.018554 | 0.0031441 | 0.024105 |  | 1 | 0 | 0 | 0
SF | 5267.493 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 418.507 | 2.0782 | 0.0076996 | 0.0013065 | 0.010017 |  | 0 | 1 | 0 | 0
SF | 5281.043 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 404.957 | 2.0109 | 0.0074503 | 0.0012691 | 0.0097298 |  | 0 | 1 | 0 | 0
SD | 5285.893 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 400.107 | 3.0665 | 0.017535 | 0.0029913 | 0.022933 |  | 1 | 0 | 0 | 0
SD | 5301.543 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 384.457 | 2.9465 | 0.016849 | 0.0028884 | 0.022144 |  | 1 | 0 | 0 | 0
SF | 5306.393 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 379.607 | 1.885 | 0.0069839 | 0.0011992 | 0.0091935 |  | 0 | 1 | 0 | 0
SF | 5319.943 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 366.057 | 1.8177 | 0.0067346 | 0.0011618 | 0.0089068 |  | 0 | 1 | 0 | 0
SD | 5324.793 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 361.207 | 2.7683 | 0.01583 | 0.0027355 | 0.020973 |  | 1 | 0 | 0 | 0
SD | 5340.443 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 345.557 | 2.6484 | 0.015144 | 0.0026327 | 0.020184 |  | 1 | 0 | 0 | 0
SF | 5345.293 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 340.707 | 1.6919 | 0.0062682 | 0.0010918 | 0.0083705 |  | 0 | 1 | 0 | 0
SF | 5358.843 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 327.157 | 1.6246 | 0.0060189 | 0.0010544 | 0.0080838 |  | 0 | 1 | 0 | 0
SD | 5363.693 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 322.307 | 2.4702 | 0.014125 | 0.0024798 | 0.019012 |  | 1 | 0 | 0 | 0
SD | 5379.343 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 306.657 | 2.3503 | 0.013439 | 0.0023769 | 0.018223 |  | 1 | 0 | 0 | 0
SF | 5384.193 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 301.807 | 1.4987 | 0.0055526 | 0.00098445 | 0.0075474 |  | 0 | 1 | 0 | 0
SF | 5397.743 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 288.257 | 1.4314 | 0.0053033 | 0.00094706 | 0.0072608 |  | 0 | 1 | 0 | 0
SD | 5402.593 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 283.407 | 2.1721 | 0.01242 | 0.0022241 | 0.017051 |  | 1 | 0 | 0 | 0
SD1 | 5418.243 | 0.25 | 0 | 0 | 0 | 0 | 267.757 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1 | 0
SF1 | 5423.093 | 0.25 | 0 | 0 | 0 | 0 | 262.907 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1
SF1 | 5683.867 | 0.25 | 0 | 0 | 0 | 0 | 2.133 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1
SD1 | 5688.717 | 0.25 | 0 | 0 | 0 | 0 | 2.717 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1 | 0
SD | 5704.367 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 18.367 | 0.14077 | 0.00080494 | 0.00048179 | 0.0036937 |  | 1 | 0 | 0 | 0
SF | 5709.217 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 23.217 | 0.11529 | 0.00042714 | 0.00021564 | 0.0016532 |  | 0 | 1 | 0 | 0
SF | 5722.767 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 36.767 | 0.18257 | 0.00067643 | 0.00025303 | 0.0019399 |  | 0 | 1 | 0 | 0
SD | 5727.617 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 41.617 | 0.31896 | 0.0018239 | 0.00063463 | 0.0048655 |  | 1 | 0 | 0 | 0
SD | 5743.267 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 57.267 | 0.4389 | 0.0025097 | 0.00073751 | 0.0056542 |  | 1 | 0 | 0 | 0
SF | 5748.117 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 62.117 | 0.30846 | 0.0011428 | 0.00032299 | 0.0024762 |  | 0 | 1 | 0 | 0
SF | 5761.667 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 75.667 | 0.37574 | 0.0013921 | 0.00036038 | 0.0027629 |  | 0 | 1 | 0 | 0
SD | 5766.517 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 80.517 | 0.61709 | 0.0035287 | 0.00089035 | 0.006826 |  | 1 | 0 | 0 | 0
SD | 5782.167 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 96.167 | 0.73704 | 0.0042146 | 0.00099323 | 0.0076147 |  | 1 | 0 | 0 | 0
SF | 5787.017 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 101.017 | 0.50162 | 0.0018585 | 0.00043034 | 0.0032993 |  | 0 | 1 | 0 | 0
SF | 5800.567 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 114.567 | 0.56891 | 0.0021078 | 0.00046773 | 0.0035859 |  | 0 | 1 | 0 | 0
SD | 5805.417 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 119.417 | 0.91523 | 0.0052335 | 0.0011461 | 0.0087865 |  | 1 | 0 | 0 | 0
SD | 5821.067 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 135.067 | 1.0352 | 0.0059194 | 0.0012489 | 0.0095753 |  | 1 | 0 | 0 | 0
SF | 5825.917 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 139.917 | 0.69479 | 0.0025742 | 0.00053769 | 0.0041223 |  | 0 | 1 | 0 | 0
SF | 5839.467 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 153.467 | 0.76207 | 0.0028234 | 0.00057508 | 0.004409 |  | 0 | 1 | 0 | 0
SD | 5844.317 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 158.317 | 1.2134 | 0.0069383 | 0.0014018 | 0.010747 |  | 1 | 0 | 0 | 0
SD | 5859.967 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 173.967 | 1.3333 | 0.0076242 | 0.0015047 | 0.011536 |  | 1 | 0 | 0 | 0
SF | 5864.817 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 178.817 | 0.88795 | 0.0032898 | 0.00064504 | 0.0049453 |  | 0 | 1 | 0 | 0
SF | 5878.367 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 192.367 | 0.95524 | 0.0035391 | 0.00068243 | 0.005232 |  | 0 | 1 | 0 | 0
SD | 5883.217 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 197.217 | 1.5115 | 0.0086431 | 0.0016575 | 0.012708 |  | 1 | 0 | 0 | 0
SD | 5898.867 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 212.867 | 1.6314 | 0.009329 | 0.0017604 | 0.013496 |  | 1 | 0 | 0 | 0
SF | 5903.717 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 217.717 | 1.0811 | 0.0040055 | 0.00075239 | 0.0057683 |  | 0 | 1 | 0 | 0
SF | 5917.267 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 231.267 | 1.1484 | 0.0042548 | 0.00078978 | 0.006055 |  | 0 | 1 | 0 | 0
SD | 5922.117 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 236.117 | 1.8096 | 0.010348 | 0.0019132 | 0.014668 |  | 1 | 0 | 0 | 0
SD | 5937.767 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 251.767 | 1.9296 | 0.011034 | 0.0020161 | 0.015457 |  | 1 | 0 | 0 | 0
SF | 5942.617 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 256.617 | 1.2743 | 0.0047212 | 0.00085974 | 0.0065913 |  | 0 | 1 | 0 | 0
SF | 5956.167 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 270.167 | 1.3416 | 0.0049705 | 0.00089713 | 0.006878 |  | 0 | 1 | 0 | 0
SD | 5961.017 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 275.017 | 2.1078 | 0.012053 | 0.002169 | 0.016629 |  | 1 | 0 | 0 | 0
SD | 5976.667 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 290.667 | 2.2277 | 0.012739 | 0.0022718 | 0.017417 |  | 1 | 0 | 0 | 0
SF | 5981.517 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 295.517 | 1.4675 | 0.0054368 | 0.00096709 | 0.0074144 |  | 0 | 1 | 0 | 0
SF | 5995.067 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 309.067 | 1.5347 | 0.0056861 | 0.0010045 | 0.007701 |  | 0 | 1 | 0 | 0
SD | 5999.917 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 313.917 | 2.4059 | 0.013758 | 0.0024247 | 0.018589 |  | 1 | 0 | 0 | 0
SD | 6015.567 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 329.567 | 2.5258 | 0.014443 | 0.0025276 | 0.019378 |  | 1 | 0 | 0 | 0
SF | 6020.417 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 334.417 | 1.6606 | 0.0061525 | 0.0010744 | 0.0082374 |  | 0 | 1 | 0 | 0
SF | 6033.967 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 347.967 | 1.7279 | 0.0064018 | 0.0011118 | 0.0085241 |  | 0 | 1 | 0 | 0
SD | 6038.817 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 352.817 | 2.704 | 0.015462 | 0.0026804 | 0.02055 |  | 1 | 0 | 0 | 0
SD | 6054.467 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 368.467 | 2.824 | 0.016148 | 0.0027833 | 0.021338 |  | 1 | 0 | 0 | 0
SF | 6059.317 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 373.317 | 1.8538 | 0.0068682 | 0.0011818 | 0.0090604 |  | 0 | 1 | 0 | 0
SF | 6072.867 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 386.867 | 1.9211 | 0.0071175 | 0.0012192 | 0.0093471 |  | 0 | 1 | 0 | 0
SD | 6077.717 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 391.717 | 3.0022 | 0.017167 | 0.0029361 | 0.02251 |  | 1 | 0 | 0 | 0
SD | 6093.367 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 407.367 | 3.1221 | 0.017853 | 0.003039 | 0.023299 |  | 1 | 0 | 0 | 0
SF | 6098.217 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 412.217 | 2.047 | 0.0075839 | 0.0012891 | 0.0098834 |  | 0 | 1 | 0 | 0
SF | 6111.767 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 425.767 | 2.1142 | 0.0078331 | 0.0013265 | 0.01017 |  | 0 | 1 | 0 | 0
SD | 6116.617 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 430.617 | 3.3003 | 0.018872 | 0.0031918 | 0.024471 |  | 1 | 0 | 0 | 0
SD | 6132.267 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 446.267 | 3.4202 | 0.019558 | 0.0032947 | 0.02526 |  | 1 | 0 | 0 | 0
SF | 6137.117 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 451.117 | 2.2401 | 0.0082995 | 0.0013965 | 0.010706 |  | 0 | 1 | 0 | 0
SF | 6150.667 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 464.667 | 2.3074 | 0.0085488 | 0.0014339 | 0.010993 |  | 0 | 1 | 0 | 0
SD | 6155.517 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 469.517 | 3.5984 | 0.020577 | 0.0034476 | 0.026431 |  | 1 | 0 | 0 | 0
SD | 6171.167 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 485.167 | 3.7184 | 0.021263 | 0.0035504 | 0.02722 |  | 1 | 0 | 0 | 0
SF | 6176.017 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 490.017 | 2.4333 | 0.0090152 | 0.0015038 | 0.011529 |  | 0 | 1 | 0 | 0
SF | 6189.567 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 503.567 | 2.5006 | 0.0092645 | 0.0015412 | 0.011816 |  | 0 | 1 | 0 | 0
SD | 6194.417 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 508.417 | 3.8966 | 0.022282 | 0.0037033 | 0.028392 |  | 1 | 0 | 0 | 0
SD | 6210.067 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 524.067 | 4.0165 | 0.022967 | 0.0038062 | 0.029181 |  | 1 | 0 | 0 | 0
SF | 6214.917 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 528.917 | 2.6265 | 0.0097309 | 0.0016112 | 0.012352 |  | 0 | 1 | 0 | 0
SF | 6228.467 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 542.467 | 2.6937 | 0.0099802 | 0.0016486 | 0.012639 |  | 0 | 1 | 0 | 0
SD | 6233.317 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 547.317 | 4.1947 | 0.023986 | 0.003959 | 0.030352 |  | 1 | 0 | 0 | 0
SD | 6248.967 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 562.967 | 4.3146 | 0.024672 | 0.0040619 | 0.031141 |  | 1 | 0 | 0 | 0
SF | 6253.817 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 567.817 | 2.8196 | 0.010447 | 0.0017185 | 0.013176 |  | 0 | 1 | 0 | 0
SF | 6267.367 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 581.367 | 2.8869 | 0.010696 | 0.0017559 | 0.013462 |  | 0 | 1 | 0 | 0
SD | 6272.217 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 586.217 | 4.4928 | 0.025691 | 0.0042147 | 0.032313 |  | 1 | 0 | 0 | 0
SD | 6287.867 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 601.867 | 4.6128 | 0.026377 | 0.0043176 | 0.033102 |  | 1 | 0 | 0 | 0
SF | 6292.717 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 606.717 | 3.0128 | 0.011162 | 0.0018259 | 0.013999 |  | 0 | 1 | 0 | 0
SF | 6306.267 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 620.267 | 3.0801 | 0.011411 | 0.0018633 | 0.014285 |  | 0 | 1 | 0 | 0
SD | 6311.117 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 625.117 | 4.791 | 0.027396 | 0.0044704 | 0.034273 |  | 1 | 0 | 0 | 0
SD | 6326.767 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 640.767 | 4.9109 | 0.028082 | 0.0045733 | 0.035062 |  | 1 | 0 | 0 | 0
SF | 6331.617 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 645.617 | 3.2059 | 0.011878 | 0.0019332 | 0.014822 |  | 0 | 1 | 0 | 0
SF | 6345.167 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 659.167 | 3.2732 | 0.012127 | 0.0019706 | 0.015108 |  | 0 | 1 | 0 | 0
SD | 6350.017 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 664.017 | 5.0891 | 0.029101 | 0.0047262 | 0.036234 |  | 1 | 0 | 0 | 0
SD | 6365.667 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 679.667 | 5.2091 | 0.029787 | 0.004829 | 0.037023 |  | 1 | 0 | 0 | 0
SF | 6370.517 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 684.517 | 3.3991 | 0.012594 | 0.0020406 | 0.015645 |  | 0 | 1 | 0 | 0
SF | 6384.067 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 698.067 | 3.4664 | 0.012843 | 0.002078 | 0.015931 |  | 0 | 1 | 0 | 0
SD | 6388.917 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 702.917 | 5.3872 | 0.030806 | 0.0049819 | 0.038194 |  | 1 | 0 | 0 | 0
SD | 6404.567 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 718.567 | 5.5072 | 0.031491 | 0.0050848 | 0.038983 |  | 1 | 0 | 0 | 0
SF | 6409.417 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 723.417 | 3.5923 | 0.013309 | 0.0021479 | 0.016468 |  | 0 | 1 | 0 | 0
SF | 6422.967 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 736.967 | 3.6596 | 0.013559 | 0.0021853 | 0.016754 |  | 0 | 1 | 0 | 0
SD | 6427.817 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 741.817 | 5.6854 | 0.03251 | 0.0052376 | 0.040155 |  | 1 | 0 | 0 | 0
SD | 6443.467 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 757.467 | 5.8053 | 0.033196 | 0.0053405 | 0.040944 |  | 1 | 0 | 0 | 0
SF | 6448.317 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 762.317 | 3.7854 | 0.014025 | 0.0022553 | 0.017291 |  | 0 | 1 | 0 | 0
SF | 6461.867 | 0.25 | 0.1555 | 3.7049 | 0.27273 | 0.0010104 | 775.867 | 3.8527 | 0.014274 | 0.0022927 | 0.017577 |  | 0 | 1 | 0 | 0
SD | 6466.717 | 0.25 | -0.24 | 5.7183 | 0.42093 | 0.002407 | 780.717 | 5.9835 | 0.034215 | 0.0054933 | 0.042116 |  | 1 | 0 | 0 | 0
SD1 | 6482.367 | 0.25 | 0 | 0 | 0 | 0 | 796.367 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1 | 0
SF1 | 6487.217 | 0.25 | 0 | 0 | 0 | 0 | 801.217 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1
Maximum |  |  | 0.1555 | [7 empty] | 0.042779 | No. Magnets | 240 | 240 | 12 | 12
Total | [5 empty] | 0.82018 | 212691.9299 |  | 6.3505 | 1.0756 | 8.289 | Average 1-way alcove distance (m) | 425.2493 | 425.2493 | 357.8077 | 356.5465
Average | [6 empty] | 422.0078