ILC Damping Rings Component/Subsystem Specification

Part I – Classification Information

| Component Description: | Positron Damping Ring Tunnel |  |  |  |
| --- | --- | --- | --- | --- |
| Component Location (beamline): | PDR1/PDR2 | Lattice Version: |  | OCS6, 2006-06-20 |
| Document Number: | PDR1-CONV-tnl-001 |  | Date: | 2006-08-22 |
| Prepared by: | Andy Wolski |  | email: | a.wolski@dl.ac.uk |
| Technical/Global System: | CF&S |  |  |  |
| Technical/Global System Contact: | Tom Lackowski |  | email: | tomski@fnal.gov |
| DR Area System Contact: | Andy Wolski |  | email: | a.wolski@dl.ac.uk |

Part II – Main Parameters

| Parameter | Value | # Reference |
| --- | --- | --- |
| Number of beamlines in tunnel | 2 | BCD |
| Humidity control requirement | Yes |  |
| Maximum tunnel temperature | 110F (43C) | [1] |
| Tunnel access frequency |  |  |
| Tunnel total length (ring circumference) | 6695 m | [2] |
| Tunnel diameter | 4 m |  |
| Tunnel cost/meter | Public version: no costs information shown | [3] |

Part IIA – Non-wiggler Magnet and Magnet Power Supplies Parameters

| Parameter | Value | # Reference |
| --- | --- | --- |
| Magnets technology | Normal conducting electromagnet | BCD |
| Dipole max width | 346 mm | [4] |
| Dipole max length | 6.140 m | [4] |
| Dipole max weight | 1550 kg | [4] |
| Quadrupole max width | [To be provided by Magnet Systems Technical Group] |  |
| Quadrupole max length | [To be provided by Magnet Systems Technical Group] |  |
| Quadrupole max weight | [To be provided by Magnet Systems Technical Group] |  |
| Magnet service access | From one side only |  |
| Power supply locations | Every x meters |  |
| Power supplies dimensions | [To be provided by Magnet Systems Technical Group] |  |
| Power supplies weight | [To be provided by Magnet Systems Technical Group] |  |
| Power supplies quantities | [To be provided by Magnet Systems Technical Group] |  |
| Total magnets power requirement | See Power Budget (section III) |  |
| Magnets power to cooling water | See Power Budget (section III) |  |
| Magnets power to air | See Power Budget (section III) |  |

Part IIB – Wiggler Parameters

| Parameter | ## Value | # Reference |
| --- | --- | --- |
| Wiggler technology | Superferric | BCD |
| Wiggler length | 4 locations with ~ 50 m per location per ring (2 rings) |  |
| Wiggler width |  |  |
| Wiggler weight |  |  |
| Total wiggler radiation power | See Power Budget (section III) |  |
| Radiation power to cooling water | See Power Budget (section III) |  |
| Radiation power to air | See Power Budget (section III) |  |
| Total cryogenic power |  |  |

ILC Damping Rings Component Specification

| Document Number: | PDR1-CONV-tnl-001 | Date: | 2006-08-22 |
| --- | --- | --- | --- |

Part IIC – RF Parameters

| Parameter | Value | # Reference |
| --- | --- | --- |
| RF system | Superconducting | BCD |
| RF cavity cryomodule quantities | 16 per ring (in four locations) |  |
| RF cavity cryomodule length | ~ 3.5 m | [5] |
| RF cavity cryomodule width | ~ 1.5 m | [5] |
| RF cavity cryomodule weight | [To be provided by RF Power Technical Group] |  |
| RF cavity cryomodule service access | From both sides |  |
| Klystrons dimensions | [To be provided by RF Power Technical Group] |  |
| Klystrons weight | [To be provided by RF Power Technical Group] |  |
| Klystrons quantities | 4 per ring (in four locations) |  |
| Total RF power requirement | See Power Budget (section III) |  |
| RF power to cooling water | See Power Budget (section III) |  |
| RF power to air | See Power Budget (section III) |  |
| RF power to beam | See Power Budget (section III) |  |

Part III – Other Parameters, Information, and Drawings

Power Budget:

|  | Input kW |  | Duty factor | Output kW |  |  | Location |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Wall-plug | From beam |  | To beam | To water | To air |  |
| RF Power (base value) | 6300 | 0 | 1.00 | 3500 | 2300 | 500 | Alcoves |
| RF Power (peak overhead) | 700 | 0 | 0.10 | 0 | 70 | 0 | Tunnel |
| Water-cooled magnets1 | 2198 | 0 | 1.00 | 0 | 2198 | 0 | Tunnel |
| Air-cooled magnets2 | 218 | 0 | 1.00 | 0 | 0 | 218 | Tunnel |
| Cables | 2754 | 0 | 1.00 | 0 | 0 | 2754 | Tunnel |
| Magnet power supply losses | 728 | 0 | 1.00 | 0 | 0 | 728 | Alcoves |
| Injection/extraction kickers (avg) | 886 | 0 | 1.00 | 0 | 886 | 0 | Tunnel |
| Radiation | 0 | 3500 | 1.00 | 0 | 2800 | 700 | Tunnel |
| Total | 13784 |  |  |  | 8254 | 4900 |  |

1 Dipoles, quadrupoles and septa.

2 Sextupoles, orbit correctors and skew quadrupoles.

ILC Damping Rings Component Specification

| Document Number: | PDR1-CONV-tnl-001 | Date: | 2006-08-22 |
| --- | --- | --- | --- |

Tunnel layouts and drawings are given in: EDR-CONV-tnl-001a.pdf EDR-CONV-tnl-001b.pdf

Part IV – References

[1]	Private communication (email), Emil Huedem, 2006-06-13.

[2]	OCS6, Lattice design 2006-06-20

https://wiki.lepp.cornell.edu/ilc/bin/view/Public/DampingRings/WebHome

[3]	CF&S Spreadsheet DR_cut_CFS_Cost_Draft_6_30_06.

[4]	6 m dipole.  Component Specification Sheet: EDR-MAG-dip-002.

[5]	Based on CESR-c or KEK-B cryomodules