## Slide 1: CRYOGENICS FOR MLC
Eric Smith
Internal Review of MLC

## Slide 2: Outline of Discussion
Operational heat loads for 1.8K, 5K, 40K systems, per cryomodule.
Rationale for cooling by convective helium flow.
Cartoon view of cryogen distribution within the cryomodule.
Pressure drops and mass flow rates in normal operation --1.8K system
-- 5K system
-- 40K system
Cooldown requirements/constraints—main focus on 1.8K system
Differences between single module test and full linac string

## Slide 3: Operational Heat Loads
These are design heat loads. Allow for a factor of 1.5 as a safety margin.
Per module | Heat load (W) | g/s helium
1.8K static | 5.7 | 0.26
1.8K dynamic | 69.0 | 3.13
1.8K total | 74.7 | 3.39
4.5-6.0K static | 64.3 | 4.76
4.5-6.0K dynamic | 25.6 | 1.89
4.5-6.0K total | 89.0 | 6.65
40-80K static | 32.6 | 0.16
40-80K dynamic | 1455.5 | 7.00
40-80K total | 1488.0 | 7.16

## Slide 4: Choices of thermal intercept temperatures
2.0 K or below is needed for cavity operation to get adequate Q factor for RF cavities. Q should be enough higher at 1.8K to pay for the cost in Carnot efficiency, gives more margin on max. RF field, should help reduce microphonic frequency shifts on cavities.
4.5K-6.0K at 3.0 bar is chosen as a thermal intercept temperature to limit the heat flow into the 1.8K system from the input couplers and HOM loads. Max temperature must be not much more than 6.0K in order to ensure low enough RF losses from degradation of superconducting properties of Nb even at fringes of cavities.

## Slide 5: Choices of thermal …… (continued)
There is a large increase in Cp of the helium gas by operating near the helium critical point, and by operating in a supercritical regime, we ensure that we have single-phase flow, which is easier to control.
40-80K helium flow at around 20 bar is chosen to give a manageable flow rate, and operate at a sensible pressure for the refrigeration plant. The thermal expansion coefficients are sufficiently low here so that temperature changes of even 40K do not present undue stresses to the composite materials used for the HOM loads. Operating the thermal radiation shield near 40K reduces any need for a 5K thermal radiation shield.

## Slide 6: Choices of thermal …… (continued)
A further reason for operating with a 40K input temperature is that there is expected to be variation in the amount of HOM power generated in different cavities, with 200W being an average expectation. If in some cavities up to 400W were to appear, it would still be possible to operate with a maximum temperature of 120K where thermal expansion is still small. A choice of helium gas rather than liquid nitrogen for the first thermal intercept temperature is partly because of safety considerations in the tunnel (LN2 not permitted in large quantities because of ODH concerns), partly to reduce microphonic noise from bubble formation in two-phase flow, partly to reduce control complications related to varied flow regime characteristics for 2-phase systems.

## Slide 7: Choices of thermal …… (continued)
Because of the very high thermal loads arising from CW rather than pulsed operation of the acclerator, it is simply not practical to use copper cooling straps to provide thermal anchoring. It has been necessary to provide helium flow through small-diameter tubes directly past the most concentrated heat sources, namely the HOM absorbers and the input couplers. For other locations in the cryostat, where the concern is for interception of much smaller static heat flows through support structures, we have whenever possible used these simpler strap structures.

## Slide 9: Primary Flow of Cryogens through Linac String
Six cryogen lines of 50 mm diameter run through an entire half-linac (35 cryomodules in one “half”, 29 in the other), 1 for supplying 2K subcooled liquid at 1.2 bar (or pre-cool gas during initial system cooldown), 1 for supplying 4.5K fluid at 3 bar, 2 for supplying 40K gas at 20 bar, 1 for returning 6K gas at near 3 bar, 1 for returning 80K gas at 18 bar. A large 270 mm diameter line returns the evaporated 1.8K gas.
Because even with these large diameter lines there are significant pressure drops along the length of the string, each cryomodule has local manifolds for supply and return fluids, with the flow division amongst modules adjusted by four valves at each cryomodule.

## Slide 10: 1.8K System, Normal Operating Mode
Helium is admitted to the 2K-2ph line from the 2K delivery line through a JT valve on each cryomodule. The valve opening is controlled to maintain a constant level (about 1/3 full) in each cryomodule. The level is monitored by a superconducting level sensor at the far end of the cryomodule from where the liquid is admitted. The helium vessels on all six RF cavities are connected to the 2K-2ph line by a “chimney” of 100 mm diameter, large enough to ensure adequate area for superfluid counterflow even in the case of a cavity operating at less than the expected Q=2e10. The center of the 2K-2ph line is connected to the 270mm HGRP at a single point near the middle of the cryomodule. The reason for the single point of connection is that near the

## Slide 11: 1.8K System continued
refrigeration end of the linac string the total mass flow is so high that the pressure drop along the length of a single cryomodule would be large enough so that a significant part of the return flow would detour through the 2K-2ph line instead of the HGRP, with flow velocities high enough to set up surface waves on the surface of the liquid-vapor interface. The choice of the center of the cryomodule for the connection point is to reduce the maximum flow velocities over the surface of the liquid-vapor interface by having the 2K-2ph line service only 3 cavities before exiting to the larger diameter pipe. Pressure will be maintained at 20 mb at the refrigerator end of the HGRP. Cavities at the far end will be 1 or 2 mbar higher at the remote end, hence somewhat warmer.

## Slide 12: 1.8K System continued
The static heat load per cryomodule is only about 10% of the dynamic heat load from the RF. It is highly unlikely that the refrigeration plant will be able to instantly adjust to a factor of ten increase in power while maintaining a stable operating pressure. The intent would be to ramp up the load gradually over a period of an hour or two with the aid of electrical heaters mounted on the 2K-2ph line, with the possibility of quickly cutting this added power to keep the total refrigeration load constant as the RF field is ramped up on the cavities. During extended periods without RF, we would prefer not to keep full power on the system, but be able to operate the cryogenic plant at reduced throughput. Optimization of ramp-up time for power will require experimentation.

## Slide 14: 4.5-6.0K Distribution System
This part of the cooling system has a much smaller contribution from the dynamic load than the other temperature intercept levels, only about 1/3 dynamic load. Similar mass flow rates per cryomodule to the 40-80K cooling tubes (because we must operate over a much smaller temperature range to preserve the Nb superconductivity properties), but much smaller pressure drops occur because of the rather greater density of the helium gas at the lower temperature. To ensure that the pressure drops between the supply manifold within each cryomodule and the return gas pipe in the same module are rather larger than the pressure drops along the cryomodule string, we have

## Slide 15: 4.5-6K Distribution (continued)
made a series combination of several intercepts for the HOM loads and the input couplers, to create a total of 3 parallel flow paths with a similar total heat load. This allows the pressure drop to be comparable to, but smaller than, the pressure drop between the main 5cm diameter supply and return lines at the far end of the cryomodule string under the conditions of a heat load 1.5x the design heat load. Individual control valves will maintain the pressure within a smaller diameter supply manifold in each cryomodule to be a constant pressure difference above the return line within that cryomodule. The overall operating point will be maintained by means of a control valve within each cryomodule.

## Slide 16: 4.5-6K Distribution (continued)
By preference, control of the valve position for maintaining the same flow rate through the small crossfeed lines would be achieved by a differential pressure gauge between the supply manifold and the return pressure. Potentially a cheaper and adequate method might be to measure inlet and outlet temperatures on the cross-feed lines, and this alternative should be considered.
Smaller heat loads at thermal intercepts for HGRP support posts, HOM supports, will be handled by means of high conductivity copper straps.

## Slide 18: 40-80K Distribution in normal operation
Helium at 40K and 20 bar pressure is supplied from the cryoplant and runs through a 50mm extrusion through the entire length of the cryomodule string, cooling in passage an aluminum shield to which the aluminum extrusion is welded. Only a tiny percentage of the total heat load is in the form of radiation into this radiation shield, so that the temperature of the gas stream is almost unchanged in this transition, although there is a significant pressure drop. At the far end of the string of cryomodules, this shield cooling tube is connected to a supply tube which runs back through the cryomodule string, with a portion of the gas extracted to a smaller manifold within each cryomodule.

## Slide 19: 40-80K Distribution in normal … (cont.)
The reason for this somewhat more complex scheme is that with the presence of a third tube, the higher pressure end of the cryomodule supply and return lines is at the same end of the string, so the pressure drops on the individual control valves is comparable on all cryomodules. Adjustment of the valve position on one cryomodule tends to cause similar pressure drops on both supply and return for other cryomodules, so there is strongly reduced interaction between valve position in different cryomodules. In the next slide is shown the pressure distribution at 1.5x design heat loads along the cryomodule string, starting with 20 bar at the inlet to the shield cooling tube.

## Slide 20: 40-80K Distribution (continued)
Chart: Pressures 40-80K at 1.5x design flow
| 35 | 34 | 33 | 32 | 31 | 30 | 29 | 28 | 27 | 26 | 25 | 24 | 23 | 22 | 21 | 20 | 19 | 18 | 17 | 16 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
P supply | 19.52 | 19.5067 | 19.494 | 19.482 | 19.4706 | 19.4598 | 19.4495 | 19.4399 | 19.4309 | 19.4224 | 19.4144 | 19.407 | 19.4 | 19.3936 | 19.3877 | 19.3822 | 19.3771 | 19.3725 | 19.3683 | 19.3645 | 19.3611 | 19.3581 | 19.3554 | 19.353 | 19.3509 | 19.3492 | 19.3477 | 19.3464 | 19.3454 | 19.3446 | 19.344 | 19.3435 | 19.3432 | 19.3431 | 19.343 | 19.3429
P return | 18.5 | 18.4999 | 18.4997 | 18.4993 | 18.4986 | 18.4976 | 18.4961 | 18.4942 | 18.4919 | 18.4889 | 18.4854 | 18.4813 | 18.4765 | 18.4709 | 18.4646 | 18.4574 | 18.4494 | 18.4405 | 18.4307 | 18.4198 | 18.408 | 18.3951 | 18.3811 | 18.3659 | 18.3495 | 18.332 | 18.3131 | 18.293 | 18.2715 | 18.2486 | 18.2243 | 18.1985 | 18.1712 | 18.1423 | 18.1119 | 18.0798
Psup. Man | 18.9 | 18.8999 | 18.8997 | 18.8993 | 18.8986 | 18.8976 | 18.8961 | 18.8942 | 18.8919 | 18.8889 | 18.8854 | 18.8813 | 18.8765 | 18.8709 | 18.8646 | 18.8574 | 18.8494 | 18.8405 | 18.8307 | 18.8198 | 18.808 | 18.7951 | 18.7811 | 18.7659 | 18.7495 | 18.732 | 18.7131 | 18.693 | 18.6715 | 18.6486 | 18.6243 | 18.5985 | 18.5712 | 18.5423 | 18.5119 | 18.4798

## Slide 21: 40-80K Distribution in normal … (cont.)
As with the 1.8K system, the dynamic heat load is by far the greatest component of the 40-80K system. In this case, it will vary roughly as the square of the beam current. To allow a smooth transition for the cryoplant while the beam current is stepped up (or down) rapidly, it will be necessary to apply in advance a ramped electrical heat of approximately the needed value in order to allow it to be switched off quickly when the beam current is stepped up suddenly. These heaters will be attached to the HOM loads, to mimic as closely as possible the actual source of the load heating.

## Slide 22: Cooldown Constraints—Main Focus on 1.8K System
We wish to keep all parts of the system within 20K of the same temperature down to below 100K during the cooldown from room temperature, in order to ensure that there is not excessive “bowing” of the cryostat because of differential thermal contraction. To achieve this, we will need the refrigeration system to be able to deliver a helium stream at each of the 1.8K, 4.5K, and 40K supply lines which is controlled at approximately 20K below the temperature of the warmest point in the system. To speed the cooling of the overall system, we need the highest mass flow rate achievable at acceptable pressures.

## Slide 24: Cooldown Constraints (cont.)
Helium is introduced through the pre-cool valve, using the same distribution line from the linac string that in normal operation is used for feeding 2K liquid to the JT valve. The helium from the pre-cool valve then is fed through smaller tubes into the bottom of each cavity at two ends, then proceeds into the 2K-2ph line, finally into the HGRP. As can be seen in the following table, the majority of the heat capacity which needs to be cooled down resides in the HGRP, which is reached last by the pre-cool gas. Thus the cavities will drop in temperature much faster than will the HGRP, so inlet temperature needs to be kept

## Slide 25: Cooldown Constraints (cont.)

## Slide 26: Cooldown Constraints (cont.)
within 20K of the temperature of the warmest part of the HGRP. If we wish to keep the pressure of the inlet gas below 2 bar (might be necessary, depending on bypass valving in refrigerator and maximum pressure acceptable to brazed aluminum heat exchangers), a maximum flow rate of about 5 g/s per cryomodule would be available because of the pressure drop along the entire string, with the low density of the helium gas at near room temperature and only 2 bar pressure. This would permit about a 4K/hr cooling rate.

## Slide 27: Cooldown Constraints (cont.)
Although the heat capacity of the aluminum radiation shield, to be eventually cooled to 40K, is actually rather higher than that of the HGRP, this part of the system is designed to operate at higher pressures, so the mass flow rate that can be provided is much higher. Again, the key is to keeping the inlet temperature essentially the same as the inlet temperature for the gas flowing through the “2K” system.
Finally, for the 4.5K cooling line, much smaller heat capacities need to be cooled, so this again needs inlet temperature control, but flow rate should not be a problem.

## Slide 28: Differences for Single Cryomodule Test
We will be testing an individual cryomodule in one or more configurations prior to producing 64 of them. This will be done using relatively minor modifications of the cryogenic infrastructure in Wilson Laboratory, and a few differences will be needed in the cooling scheme.
1) We have no convenient way to produce an efficient 40K cooling in the laboratory currently. Thus we will be using an 80K coolant stream, similar to what we have been using in testing of the Injector CryoModule and the Horizontal Test Cryostat for a single 7-cell cavity. This means that the HOM loads will rise to a temperature of 120K under a 200W test, not 80K. This, in turn, will result

## Slide 29: Differences for Single Cryomodule Test (cont.)
in slightly higher static heat loads on the 5K system. In initial testing without an actual beam through the cavity system, we will only be able to test the cooling capacity of the system by simulation of the heat loads by electrical heaters. We will still be able to verify the static heat loads under the eventual normal operating conditions, and will still be able to test the operation of the control valve under realistic conditions, and to verify the uniformity of the parallel gas flow through the different HOM load/input coupler sets in the cryomodule.
2) Somewhat different end-cap arrangements need to be made at each end of the cryomodule, rather than the

## Slide 30: Differences for Single Cryomodule Test (cont.)
direct welding of the trunk distribution lines from one cryomodule to the next through expansion compensation bellows. Thus we don’t get quite a full test of the intermodule assembly procedure.
3) During initial cooldown of the system, in the individual cryomodule test (and in the end cryomodules of each string in the eventual full ERL), the far end of the HGRP from the return pipe to the refrigeration system does not see an effective convective gas flow beyond the point in the middle of the cryostat where the pre-cool gas from the 2K-2ph line enters. Quick calculation shows that the thermal conductivity of the titanium HGRP fails by orders

## Slide 31: Differences for Single Cryomodule Test (cont.)
of magnitude to maintain similar temperatures at the middle and end of the HGRP. We have considered two potential solutions to resolve this issue. One is to add a second connecting pipe (and bellows) connecting between the HGRP and the 2K-2ph tube at the far end of the cryomodule, permitting some flow to continue through the entire HGRP. The second is to add some sort of baffle on the inside of the HGRP to force the flow exiting from the connection chimney to proceed down to the end of the HGRP before making its return to the refrigerator. Which approach to take is still undecided, with each of the possibilities having its proponents.

## Slide 32: Other Odds and Ends
At each end of the cryomodule we need to connect to the next cryomodule for the main pumping line and each of the 6 trunk lines for the cryogen distribution through the length of the string. Because of the cold tubes shrinking relative to the outside of the cryomodule, we need a short bellows section in each line. These bellows need an external braid to prevent squirm under high pressure when cold, and need to be pre-compressed on room-temperature assembly, since the braid prevents elongation. Further, it would be desirable to have a smooth liner to reduce unnecessary turbulence induced by gas flow past the corrugations.